| PART 1 - GENERAL |  |
| --- | --- |
| 1.1 RELATED SECTIONS | .1 Section 21 12 01 – Standpipe and Hose Systems. |
| 1.2 REFERENCES | .1 Manitoba Workplace Safety and Health /Workplace Hazardous Materials Information System (WHMIS) .1 Material Safety Data Sheets (MSDS). .2 National Fire Protection Association (NFPA) .1 NFPA 10-2007, Standard for Portable Fire Extinguishers. .3 Underwriter's Laboratories Canada (ULC) .1 CAN/ULC S503-05, Standard for Carbon Dioxide Fire Extinguishers. .2 CAN/ULC S508-02, Rating and Testing of Fire Extinguishers Extinguishing Agents. |
| 1.3 DESIGN PERFORMANCE REQUIREMENTS | .1 Fire extinguishers shall be provided as required by the MBC, MFC and NFPA 10 codes. .2 Type and location of extinguishers must provide complete fire protection coverage in accordance with NFPA reference standard. .3 Provide extinguisher type and capacity most suitable to extinguish fire in area served. |
| 1.4 QUALITY ASSURANCE | .1 Equipment: ULC listed, to NFPA. .2 Extinguisher Ratings: CAN/ULC S508. .3 Health and Safety: .1 Do construction occupational health and safety in accordance with Manitoba Workplace Safety and Health Requirements. .4 COR Certification: .1 All members of the Design Build Team are to be COR Certified to participate in the design, construction and commissioning. |
| 1.5 WASTE MANAGEMENT AND DISPOSAL | .1 Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 19 – Construction/Demolition Waste Management and Disposal. |
| PART 2 - PRODUCTS |  |
| 2.1 FIRE EXTINGUISHERS | .1 Manual Fire Extinguishers: .1 Type: multi-purpose dry chemical, stored pressure and cartridge operated rechargeable type, with hose and shut-off nozzle, pressure gauge and signage. .2 ULC labeled for Type A, B, C protection. .3 Capacity: minimum 2A 10BC rating. .2 Wheeled Fire Extinguishers: .1 Material: multi-purpose cylinder, suitable for passage through standard doorway, large diameter rubber tread wheels, non kinking hose, ball type shut off nozzle and wheel valve. .2 Type: CAN/ULC S503, B and C rated, pressurized with nitrogen. .3 Capacity: up to 150 kg. .4 Discharge time: 70 sec. .5 Discharge range: 9 - 12 m. |
| 2.2 FIRE BLANKETS | .1 Silicone coated fibreglass in metal container. .2 Size: minimum 1800 x 1800 mm. |
| PART 3 - EXECUTION |  |
| 3.1 MANUFACTURER'S INSTRUCTIONS | .1 Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet. |
| 3.2 INSTALLATION | .1 Install fire extinguishers to NFPA 10 and local regulatory requirements. .1 In finished office areas, extinguishers shall be mounted in bubble-front recessed cabinets with finger latch on hinged door, or inside of standpipe and hose cabinets if the building is so equipped. .2 In clean shop areas, the extinguishers shall be mounted on a vehicle harness on the wall within an exit and access to exit. .3 In dirty or wet shop areas, such as the Woodwork Shop, Grass Seed and Fertilizer Storage or Wash Bay, the extinguisher shall be mounted inside of a surface mounted cabinet with hinged door and finger latch. .2 Dry nitrogen cartridge operated multipurpose dry chemical fire extinguishers with non-conductive hose, ABC rating, pressure gauge and signage to indicate its location mounted in surface-mounted break-glass scored plastic front cabinets with lock mechanism to prevent theft or unauthorized access are to be used in all unheated or outdoor areas. .3 Install fire blankets within shop and vehicle garage areas at locations that can be reached from corners of space by occupant travel pathways not exceeding 23 m. .4 Provide highly visible signage to indicate the locations of fire extinguishers and fire blankets. |
| 3.3 FIELD QUALITY CONTROL | .1 Verification requirements in accordance with Section 01 47 13 – LEED Requirements. |