| PART 1 - GENERAL |  |
| --- | --- |
| 1.1 SUMMARY | .1 Section Includes: .1 Materials and installation for sanitary waste and includes performance specification information for waste and vent piping, waste piping specialties, waste piping equipment and waste piping insulation. .2 Waste and Vent Piping Systems: .1 PVC pipe for buried and exposed pipe. .3 Waste Piping Specialties: .1 Clean-outs and clean-out access covers. .2 Floor drains. .3 Area drains. .4 Planter drains. .5 Sumps. .6 Grease traps. .7 Grit traps. .8 Oil/Water Separators. .4 Waste Piping Equipment: .1 Submersible sump and sewage pumps. .5 Waste Piping Insulation: .6 Sustainable requirements for construction and verification. .1 Energy efficiency. .2 Waster conservation. .3 Environmental protection. |
| 1.2 RELATED SECTIONS | .1 Section 01 33 00 – Submittal Procedures. .2 Section 01 47 13 – LEED Requirements .3 Section 01 74 11 – Cleaning. .4 Section 01 74 19 – Construction Waste Management and Disposal. .5 Section 01 78 00 – Closeout Submittals. .6 Section 01 91 13 – General Commissioning (Cx) Requirements. .7 Section 22 42 02 – Plumbing Fixtures. |
| 1.3 REFERENCES | .1 American Society for Testing and Materials International (ASTM) .1 ASTM C547-07e1, Standard Specification for Mineral Fiber Pipe Insulation. .2 ASTM D2564-04 (2009)e1, Standard Specification for Solvent Cements for Poly(Vinyl Chloride) (PVC) Plastic Piping Systems. .2 Canadian General Standards Board (CGSB) .1 CAN/CGSB 51-GP-52M-89, Vapour Barrier, Jacket and Facing Material for Pipe, Duct and Equipment Thermal Insulation. .3 Canadian Standards Association (CSA International) .1 CAN/CSA-B1800-06/B181.2-06, PVC Drain, Waste and Vent Pipe and Pipe Fittings. .2 CAN/CSA-B1800-06/B182.11-06, Recommended Practice for the Installation of Thermoplastic Drain, Storm and Sewer Pipe and Fittings. .4 Manitoba Workplace Safety and Health Workplace Hazardous Materials Information System (WHMIS) .1 Material Safety Data Sheets (MSDS). .5 National Plumbing Code Of Canada 2010 as amended by the Manitoba Plumbing Code Regulation 32/2011. |
| 1.4 PERFORMANCE REQUIREMENTS | .1 Design sanitary waste systems and install components in accordance with applicable regulations of the National Plumbing Code of Canada 2010 as amended by the Manitoba Plumbing Code Regulation 32/2011. .2 Provide water and drainage connections to equipment furnished by the Contract Administrator. .3 Design system to accommodate sanitary waste piping from fixtures in facility with allowance for future expansion to the east of the building as shown on drawings in Appendix B4. .4 Design grade for horizontal sanitary waste piping: minimum 1% in direction of flow. .5 Route pipes in an orderly manner, and maintain proper grades. .6 Design piping routing located above grade in visible locations parallel to walls and adjacent building elements. .7 Design building connections to street main: minimum of 2400 mm cover over pipe below finished grade. |
| 1.5 SUBMITTALS | .1 Submittals in accordance with Section 01 33 00 – Submittal Procedures. .2 Co-ordinate submittal requirements and provide submittals required by Section 01 47 13 – LEED Requirements. .3 Product Data: .1 Submit manufacturer's printed product literature, specifications and data sheet for fixtures and equipment. .2 Submit WHMIS MSDS in accordance with Section 01 47 13 – LEED Requirements. Indicate VOC's for adhesive and solvents during application and curing. .4 Shop Drawings: .1 Submit Shop Drawings to indicate project layout, load calculations and vent pipe sizing. .1 Vertical and horizontal piping locations and elevations and connections details. .2 Drain and trap locations, size, type, anchor and installation details, and finishes. .3 Submit shop drawings for packaged submersible pumps and controls. .4 Other details including grit separators and oil/water separators. .2 Submit full size sample of actual product, adhesive or solvent as follows: .1 Backwater valve. .2 Deep seal P-trap. .3 Drain: roof and floor. .4 Clean outs. .5 Access covers. .3 Submit information on operating mechanisms and electrical connections, finishes and location of manufacturer's nameplates. .4 Submit catalogue details for types of drain, separators neutralizer, trap, pump illustrating profiles, dimensions and methods of assembly. .5 Include schedule identifying units and their locations. .5 Test Reports: submit certified test reports from approved independent testing laboratories indicating compliance with specifications for specified performance characteristics and physical properties. .6 Certificates: submit certificates signed by manufacturer, certifying that materials comply with specified performance characteristics and physical properties. .7 Instructions: .1 Submit manufacturer's installation instructions. .2 Submit manufacturer's instructions for commissioning activities for equipment provided in this Section. .8 Manufacturer's Field Services: submit 3 copies of manufacturer's field reports. .9 Closeout submittals: submit maintenance and engineering data for incorporation into manual specified in Section 01 78 00 – Closeout Submittals. |
| 1.6 QUALITY ASSURANCE | .1 Utilize Design and installation personnel thoroughly familiar with systems of this type. .2 Provide multiple units from same manufacturer. .3 Pre-Installation meeting: .1 Convene a pre-installation meeting one week prior to beginning on-site installations. .4 Health and Safety: .1 Do construction occupational health and safety in accordance with Manitoba Workplace Safety and Health Requirements. .5 COR Certification: .1 All members of the Design Build Team are to be COR Certified to participate in the design, construction and commissioning. |
| PART 2 - PRODUCTS |  |
| 2.1 MATERIALS | .1 Sustainable Requirements: Refer to Section 01 47 13 – LEED Requirements. .2 Waste and Vent Piping Systems: .1 PVC Pipe Components: .1 Pipe: PVC plastic pipe to CAN/CSA-B181.2. .2 Joint and fitting components: .1 Fittings: PVC fittings to CAN/CSA-B181.2. .2 PVC solvent cement: to ASTM D 2564. .3 Waste Piping Specialties: .1 Clean-outs and clean-out access covers: .1 Provide threaded type clean-outs extended to finished floor or wall surface. Provide bolted clean-out cover plates on vertical rainwater leaders only. Ensure ample clearance at clean-out for rodding of drainage system. .2 Provide access covers for floors in unfinished areas: round with heavy wheel loading rated nickel bronze serrated frames and plates. Provide round access covers in finished areas with depressed centre section to accommodate floor finish. Provide wall clean-outs with chrome plated caps. .2 Floor drains: .1 Typical: epoxy coated cast iron body with double drainage flange, weep holes, combined two piece body, and adjustable heavy duty nickel/bronze strainer. .1 Floor drains in public areas shall be capable of receiving up to 264 litres per minute (139.5 fixture units) without water spilling out of the sloped floor area catchment of the drain, such as from a broken sprinkler head. .2 Shower and washroom floor drains: complete with a removable perforated sediment bucket. .3 Equipment rooms: complete with a polished bronze funnel type strainer and extension for floating floor. .3 Area drains: epoxy coated cast iron body, adjustable collar and galvanized ductile iron locking grate suitable for heavy equipment wheel loads. .4 Waste Pumping Equipment: .1 Submersible sump and sewage pumps: .1 Type: completely submersible, vertical, centrifugal. .2 Casing: cast iron volute and oil filled motor chamber. .3 Impeller: bronze, non-clog with corrosion resistant alloy steel shaft. .4 Bearings: anti-friction ball or roller. .5 Accessories: oil resistant power cord with three prong connector on single phase, fractional horsepower units only. .6 Duplex Controls: packaged pre-wired alternator with mercury type liquid level controls and control panel to cut in second pump on rising level or pump failure, and separate liquid level control for high level alarm. .2 Waste Oil Tanks: ULC approved; conforming to the Environmental Code of Practice for Aboveground and Underground Storage Tank Systems containing Petroleum Products and Allied Petroleum Products. .1 Tank: construction double walled or with secondary containment, gravity fed, with above ground connection to permit manual disposal and storage of other waste oil products. .2 Provide accessories and signage as required by the Manitoba Regulations 188/2001 and 19/2011. .3 Sump: reinforced concrete sumps, complete with necessary drainage fittings, 10 mm thick galvanized checkered steel plate covers with gasket seal frames anchor bolts. .4 Grease traps: .1 Epoxy finished, cast iron or acid resistant finished, welded steel and complete with flow control fitting and thermometer. .2 Waterflow and grease holding capacities as required by design. Set traps in recess in floor. .5 Oil/Water Separator: ULC approved; conforming to the Environmental Code of Practice for Aboveground and Underground Storage Tank Systems containing Petroleum Products and Allied Petroleum Products. .1 Separator: construction gravity fed, double walled, inert to petroleum products, with venting system. .2 30 year manufacturer's warranty against leakage due to internal or external corrosion or structural failure. .3 Capable of producing effluent free oil at 15 ppm. .4 Monitoring system capable of detecting leaks as small as 0.38 litre per hour with 99.9 % probability of detection and less than 1.2% probability of false alarm. .5 Waste Piping Insulation: .1 Material: 25 mm formed mineral fibre rigid insulation sleeving. .2 "K" Value: maximum 0.035 W/m. °C at 24°C mean temperature. .3 Service Temperature: -14°C to 100°C. .4 Jacket: factory applied vapour barrier jacket to CAN/CGSB 51-GP-52Ma, Type 1, with longitudinal lap seal. |
| PART 3 - EXECUTION |  |
| 3.1 MANUFACTURER'S INSTRUCTIONS | .1 Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and data sheet. |
| 3.2 INSTALLATION | .1 General. .1 Install components in accordance with CAN/CSA-B182.11. .2 Route and install piping to maintain design grades. .3 Install components to conserve headroom and space. .4 Install concealed piping close to building structure to minimize furring. .5 Group piping at common elevations. .6 Arrange piping to compensate for expansion and contraction. .2 Building sewer service connection is provided under Division 33 from 1 m outside of the building foundation. .3 Floor Drains: .1 Where floor drains are located over occupied areas, provide waterproof installation. .2 Install trap primer to floor drains. .3 Provide dedicated drains for equipment in Mechanical Room. .4 Clean Outs: lubricate clean-out plugs with mixture of graphite and linseed oil. Prior to building turnover remove clean-out plugs, re-lubricate and reinstall using enough force to ensure permanent leakproof joint. .5 Under-floor piping is to be installed, supported and sealed at floor penetrations to maintain the following: .1 Penetrations of the floor slab from underground to the main floor are to be sealed gas-tight to prevent the migration of methane gas into the aboveground spaces. .2 Make connections to floor drains, cleanouts, and floor outlet fixtures with rigid mechanical joining methods that will resist pull-out and deflection. .3 Do not use slip-joint pipe joining methods below the floor slab of any building. .4 Provide support for underground piping from the main floor slab that is both rigid, and durable to prevent changes in slope or losses in pipe integrity due to settlement, heaving or corrosion. .5 Arrange piping to compensate for pipe expansion and contraction as the soil temperature and temperature of the pipe due to its contents change. |
| 3.3 PIPE SCHEDULE | .1 Install sanitary drain and vent lines as follows: |

SERVICE    	PIPE    		FITTING     	JOINT

DWV, above  	PVC		PVC		Solvent

Grade						Weld

DWV, 		PVC		PVC		Solvent

Buried						Weld

| 3.4 INSULATION | .1 Insulate minimum of 1500 mm of plumbing vents and above ground horizontal drain lines. Insulate exposed waste lines. |
| --- | --- |
| 3.5 FIELD QUALITY CONTROL | .1 Manufacturer's Field Services. .1 Have manufacturer of products, supplied under this Section, review Work involved in handling, installation/application, protection and cleaning, of their products. Submit written reports, in format acceptable to Contract Administrator to verify compliance of Work with Contract. .2 Manufacturer's Field Services: provide manufacturer's field services consisting of product use recommendations and periodic site visits for inspection of product installation in accordance with manufacturer's instructions. .3 Schedule site visits, to review Work, at stages listed: .1 After delivery and storage of products, and when preparatory Work, or other Work, on which the Work of this Section depends, is complete but before installation begins. .2 Twice during progress of Work at 25% and 60% complete. .3 Upon completion of the Work, after cleaning is carried out. .4 Obtain reports, within 3 days of review, and submit, immediately, to Contract Administrator. .2 Verification: provide verification to Contract Administrator that drainage lines are installed with a 1% grade in the direction of flow. .3 Verification requirements in accordance with Section 01 47 13 – LEED Requirements. |
| 3.6 CLEANING | .1 Perform cleaning operations as specified in Section 01 74 11 – Cleaning and in accordance with manufacturer's recommendations. |