| PART 1 - GENERAL |  |
| --- | --- |
| 1.1 SUMMARY | .1 Section Includes: .1 Materials and installation for plumbing fixtures. .2 Sinks: .1 Lavatory Sinks. .2 Countertop Stainless Steel Sinks .3 Utility Basins. .4 Service Sinks. .3 Showers. .4 Urinals. .5 Water Closets. .6 Drinking Fountain/Cooler. .7 Emergency Eyewash Stations. .8 Other Plumbing Fixtures. .2 Related Sections: .1 Section 01 33 00 – Submittal Procedures. .2 Section 01 47 13 – LEED Requirements. .3 Section 01 74 11 – Cleaning. .4 Section 01 74 19 – Construction Waste Management and Disposal. .5 Section 01 78 00 – Closeout Submittals. .6 Section 01 91 13 – General Commissioning (Cx) Requirements. .7 Section 22 11 19 – Domestic Water Distribution. .8 Section 22 13 18 – Drainage, Waste and Vent Piping-Plastic. .9 Section 22 42 00 – Special Plumbing Systems. |
| 1.2 REFERENCES | .1 American Refrigeration Institute (ARI.) .1 ARI 1010-02, Self-Contained, Mechanically Refrigerated Drinking-Water Coolers. .2 Canadian Standards Association (CSA International) .1 CAN/CSA B45 Series-02, Plumbing Fixtures. .2 CAN/CSA B125-05, Plumbing Fittings. .3 CAN/CSA-B651-M95(R2001), Barrier-Free Design. .3 City of Winnipeg Universal Design Policy. .4 American National Standards Institute (ANSI) .1 ANSI Z358.1-04, “American National Standard for Emergency Eyewash and Shower Equipment. |
| 1.3 PERFORMANCE REQUIREMENTS | .1 Provide low flow fixtures where shown and specified. .2 Provide barrier-free fixtures where indicated and specified, to CAN/CSA-B651. |
| 1.4 SUBMITTALS | .1 Submittals in accordance with Section 01 33 00 – Submittal Procedures. .2 Coordinate submittal requirements and provide submittals required by Section 01 47 13 – LEED Requirements. .3 Product Data: .1 Submit manufacturer's printed product literature, specifications and datasheet for fixtures and equipment. .2 Submit WHMIS MSDS in accordance with Section 01 47 13 – LEED Requirements. Indicate VOC's for adhesive and solvents during application and curing. .4 Closeout submittals: submit maintenance and engineering data for incorporation into manual specified in Section 01 78 00 – Closeout Submittals. .5 Test Reports: submit certified test reports from approved independent testing laboratories indicating compliance with specifications for specified performance characteristics and physical properties. .6 Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties. .7 Manufacturer's Field Services: submit reports within 3 days of receipt from manufacturer. .8 Instructions: submit manufacturer's installation instructions. |
| 1.5 QUALITY ASSURANCE | .1 Utilize design and installation personnel thoroughly familiar with systems of this type. .2 Health and Safety: .1 Do construction occupational health and safety in accordance with Manitoba Workplace Safety and Health Requirements. .3 COR Certification: .1 All members of the Design Build Team are to be COR Certified to participate in the design, construction and commissioning. |
| 1.6 DELIVERY, STORAGE AND HANDLING | .1 Maintain piping and valve cleanliness by protecting open ends from entry by dust, water, debris or vermin during delivery and storage. .2 Material damaged in transit or during storage and handling is to be replaced prior to installations. .3 Material for use in potable water system shall be stored in a weathertight storage building or construction. |
| PART 2 - PRODUCTS |  |
| 2.1 SUSTAINABLE REQUIREMENTS | .1 Refer to Section 01 47 13 – LEED Requirements. |
| 2.2 MATERIALS | .1 Materials and resources in accordance with Section 01 47 13 – LEED Requirements. .2 Fixtures: free from flaws and blemishes, clear, smooth and bright surface finish. .3 Exposed Brass: high quality institutional grade, chrome plated. |
| 2.3 SINKS | .1 Sinks: .1 Bowl: non-staining material, self-rimming, single or double compartment with undercoating, 90 mm crumb cup strainer and discharge fitting, two (2) hole drilling in ledge back. .2 Size: Bowl 500 x 510 x 180 mm. .3 Trim: chrome plated metal supply with swing spout, aerator. .2 Lavatory Sinks: .1 Configuration: countertop, with splash lip, soap depressions, front overflow opening. .2 Material: vitreous china or stainless steel. .3 Size: 500 x 450 mm. .4 Trim: .1 Supply: aerated water supply, maximum flow rate 8.35 L/min at 413 kPa, adjustable temperature mixing controls. .2 Electronic Faucet: proximity sensor, waterproof, incorporated into unit body, impact and scratch resistant lens, manual override button. .1 Proximity Adjustment: 100 mm. .2 Run Time: 0-60 seconds maximum, adjustable. .3 Power: AC 110 volt circuit c/w transformer, UL and CSA listed. .4 Waste: washer-less, pop-up. .3 Utility Basins: .1 Basin: non-staining material, self rimming, single compartment, two (2) hole drilling to suit faucet in ledge back. .2 Trim: chrome plated with fixed spout and aerator. .4 Service and Slop Sink: .1 Bowl: 900 x 600 x 250 mm size, floor mounted sink with 25 mm wide shoulders, stainless steel strainer. .2 Trim: exposed wall type supply with cross handle, spout wall brace, vacuum breaker, hose and spout, strainer, eccentric adjustable inlets, integral screwdriver stops with covering caps and adjustable threaded wall flanges, 1.5 metre, 15 mm plain end reinforced rubber base, hose clamp, mop hanger and stainless steel backsplash for 450 mm above the top of the rim on all adjacent walls. .3 Provide stainless steel slash guards between the fixture and the adjacent wall(s) and surfaces on two sides, extending 460mm above the fixture rim up the wall. |
| 2.4 SHOWERS | .1 Stall: Fibreglass reinforced polyester with bonderized white gel coat finish. .2 Base: moulded stone with chrome plated brass waste strainer and tailpiece. .3 Shower Head: non-clogging, vandal-proof, ball joint with integral wall bracket and escutcheon, maximum 9.5 L/min flow rate at 550 kPa, suitable for handicap use. .4 Manual Taps: barrier free, stainless steel. .5 Accessories: soap dish. |
| 2.5 URINALS | .1 Type: Wall-hung automatic hands-free flush valve. .2 Vitreous china, wall-hung with floor mounted carrier system, with shields, integral trap, integral splash rim, and stainless steel strainer. .3 Hard wired power supply with battery back-up for automatic flush valves, c/w integral water stop and escutcheons, chrome finish. |
| 2.6 WATER CLOSETS | .1 Capacity: 6 litres per flush, automatic hands free operation. .2 Bowl: vitreous china, with elongated rim. .3 Hard wired power supply with battery back-up for automatic flush actuation via infrared sensor, c/w adjustable range integral water stop and escutcheons, chrome finish. In accordance with Barrier-Free design. .4 Seat: inorganic material warm to the touch, open front, with cover, self-sustaining hinge. Provide cover stop as back rest for accessible fixtures in accordance with Barrier-Free design. |
| 2.7 FOUNTAIN/COOLER | .1 Refrigerated Fountain/Cooler: semi-recessed, vandal proof cowling, hooded anti-squirt bubbler with stream guard, automatic stream regulator, pushbutton operator, mounting bracket screwdriver stop. .2 Refrigeration section: .1 Capacity: 30 L/h from 27°C to 10°C, with 32°C ambient air, to ARI 1010. .2 Electrical: grounded electrical cord with plug, CSA certified. .3 Bubbler: pushbutton operated, self-regulating, angle stream, squirt-proof, with nozzle and guard. .4 Non CFC refrigerants. .3 Barrier-Free Coolers: stainless steel with floor supported chair carrier. |
| 2.8 OTHER PLUMBING FIXTURES | .1 Thermostatic Mixing Valve: complete with check valve, volume control shut-off valve on outlet, stem type thermometer on outlet, strainer stop check on inlet, mounted in lockable cabinet. .1 When used in conjunction with emergency eyewash stations, the thermostatic mixing valve shall be fail safe to cold water flow and be set according to ANSI Z358.1-04. .2 Emergency Eye Wash Station: wall mounted, non-metallic, twin spray nozzle stay open valve, stainless steel push flag with trap according to ANSI Z358.1-04. |
| 2.9 FLOOR DRAIN | .1 Epoxy coated cast iron body with minimum 150 mm diameter adjustable nickel-bronze strainer per Section 22 13 18 – Sanitary Waste. |
| 2.10 FIXTURE PIPING | .1 Supply: flexible, non-metallic, individual shut-off valves, escutcheon at wall in exposed areas. .2 Waste: non-metallic, with P trap and cleanout on fixtures with no integral trap. |
| PART 3 - EXECUTION |  |
| 3.1 MANUFACTURER'S INSTRUCTIONS | .1 Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet. |
| 3.2 INSTALLATION | .1 Locate plumbing fixtures at locations shown on drawings, in numbers required by code and as indicated in the Program of Requirements. .2 Provide barrier free fixtures where required. .3 Seal sinks to prevent water leaks. .4 Provide flexible supplies to fixtures with screwdriver stops, reducers and escutcheons. .5 Wall Mounted Fixtures: use approved floor supported carriers to suit application. .6 Floor Mounted Fixtures: solidly attach water closets to floor with lag screws and bolt cap. Do not use lead flashing to hold closet in place. .7 Install hose and faucets and hose connections with vacuum breakers. .8 Supply tempered water to shower heads through a centrally located thermostatic mixing valve. .9 Locate thermostatic mixing valve in cabinet at approved locations. Provide one mixing valve for each shower room and one on distribution loop to eyewash basins .1 The eyewash tempered water supply loop requires constant circulation to maintain temperature and potable conditions. Provide a recirculation pump and piping system. .10 Clean exposed fixtures after installation is complete. |
| 3.3 FIELD QUALITY CONTROL | .1 Site Tests/Inspection. .1 Operate equipment and verify that performance criteria specified in this section has been achieved. .2 Pressure test piping to same standards as domestic water piping code requirements. .3 Measure delivery at emergency eyewash station and adjustable fixtures to ensure design pressure and flow performance. Adjust if necessary to meet requirements of CSA B45, CSA B125, and ANSI Z358.1. .2 Manufacturer's Field Services. .1 Have manufacturer of products, supplied under this Section, review Work involved in the handling, installation/application, protection and cleaning, of its product[s] and submit written reports to the Consultant and Owner’s Advisor, in acceptable format, to verify compliance of Work with Contract. .2 Manufacturer's Field Services: provide manufacturer's field services consisting of product use recommendations and periodic site visits for inspection of product installation in accordance with manufacturer's instructions. .3 Schedule site visits, to review Work, at stages listed: .1 After delivery and storage of products, and when preparatory Work, or other Work, on which the Work of this Section depends, is complete but before installation begins. .2 Twice during progress of Work at 25% and 60% complete. .3 Upon completion of the Work, after cleaning is carried out. .4 Obtain reports, within 3 days of review, and submit, immediately, to Consultant and Owner’s Advisor. .3 Verification requirements in accordance with Section 01 47 13 – LEED Requirements. |
| 3.4 CLEANING | .1 Perform cleaning operations as specified in Section 01 74 11 – Cleaning and in accordance with manufacturer's recommendations. |