| PART 1 - GENERAL |  |
| --- | --- |
| 1.1 RELATED SECTIONS | .1 26 05 02 - Electrical Service and Distribution .2 26 05 03 – Lighting, Power and Branch Wiring. .3 26 05 04 – Electrical Controls & Instrumentation. .4 27 05 13 – Communications Services .5 28 13 00 – Electronic Safety and Security. |
| 1.2 REFERENCES | .1 American Society of Mechanical Engineers (ASME) .1 ANSI/ASME A13.1-96, Scheme For The Identification Of Piping Systems. .2 Canadian Standards Association (CSA International) .1 CAN/CSA-B651-04, Accessible Design for the Built Environment. .2 CSA C22.1-09, Canadian Electrical Code Part I, Safety Standard for Electrical Installations and CE Code Handbook. Amendments for Provinces. .3 CSA C22.2 No.0-M91(R2001), General Requirements - Canadian Electrical Code Part II. .4 CAN/CSA-C22.3 No.3-98(R2003), Electrical Co-ordination. .6 CAN3 C235-83(R2000), Preferred Voltage Levels for AC Systems, 0 to 50,000 V. .3 Manitoba Workplace Safety & Health/Workplace Hazardous Materials Information System (WHMIS) .1 Material Safety Data Sheets (MSDS). .4 National Research Council of Canada .1 Model National Energy Code of Canada for Buildings. .5 Underwriters' Laboratories of Canada (ULC) |
| 1.3 DESIGN AND PERFORMANCE REQUIREMENTS | .1 Underground Electrical Service: CSA C22.3 No.1 and CAN/CSA-C22.3 No.3. .2 Design equipment, components, and assemblies to operate satisfactorily at 60 Hz, within normal operating limits established within CAN3 C235. .3 Provide equipment designed to operate in extreme operating limits specified in CAN3 C235, without damage to equipment or failure of service. .4 Barrier-Free access: design equipment and components in accordance with CAN/CSA-B651. .5 Comply with the Model National Energy Code of Canada for Buildings.. |
| 1.4 SUBMITTALS | .1 Submit product data in accordance with Section 01 33 00 - Submittal Procedures. .2 Submit requested documentation to the Authority having jurisdiction and the Contract Administrator. .3 Submit Workplace Safety and Health documentation including Workpalce Hazardos Materials Information System (WHMIS) MSDS - Material Safety Data Sheets acceptable to Manitoba Workplace Safety and Health for applicable electrical equipment and material. Indicate applicable VOC content. |
| 1.5 SHOP DRAWINGS | .1 Submit shop drawings in accordance with Section 01 33 00 - Submittal Procedures. .1 Shop drawings: submit drawings stamped and signed by professional engineer registered or licensed in the Province of Manitoba, Canada. .2 Indicate project layout, including details of lighting and power system structure, including wiring schematic diagrams. Indicate dimensions, capacities, weights and performance characteristics. .3 Indicate product and material data detailing of electrical and electronic equipment. |
| 1.6 SAMPLES | .1 Submit samples in accordance with Section 01 33 00 - Submittal Procedures. .2 Submit duplicate samples of equipment and components are to be submitted where requested. .3 After review and acceptance, samples will be returned for incorporation into work. |
| 1.7 DESIGN DATA | .1 Submit design data in accordance with Section 01 33 00 - Submittal Procedures. .2 Submit design calculations for the following: .1 Lighting level, interior and exterior, luminance plots. .2 Estimated electrical energy demand (summer, winter), showing connected load and diversified demand. .3 Voltage drop, as designed and at ultimate capacity. .4 Energy budget (LEED). .5 Lighting power density (W/m²). .6 Fault level calculations. .7 Coordination study. .8 Site and floor plans showing security perimeter levels and their integration with the access control, intrusion detection and CCTV field devices and control devices. |
| 1.8 TEST REPORTS | .1 Submit certified test reports and certificates to the Contract Administrator from approved independent testing laboratories. .1 Indicate compliance with specifications for specified performance characteristics and physical properties. .2 Manufacturer's Field Services: submit copies of manufacturer's field inspection reports. |
| 1.9 CERTIFICATES | .1 Submit inspection reports and certificates of acceptance from authorities having jurisdiction to the Contract Administrator at Substantial Completion. .2 Obtain and pay for necessary permits, licenses, inspections and fees required. .3 Certificates: submit certificates signed by product or component manufacturers, certifying that products comply with specified performance characteristics and physical properties. |
| 1.10 CLOSEOUT SUBMITTALS | .1 Submit operation and maintenance data for incorporation into manual specified in Section 01 78 00 - Closeout Submittals. .2 Include accurate as-built drawings. As-built drawings are to show raceway locations and raceway usage. .3 Submit two electronic copies and two paper sets of drawings and specifications. .4 Manufacturer's installation instructions: submit instructions for installation and operation of products, components, and assemblies. .5 Submit operation and maintenance manuals for electrical and electronic equipment. Including details of design elements, component function and maintenance requirements to effectively operate, maintain or repair. .6 Include technical data, product data, component illustrations, technical descriptions and parts list, wiring and schematic diagrams not considered proprietary, test and verification reports. |
| 1.11 QUALITY ASSURANCE | .1 Utilize design and installation personnel thoroughly familiar with systems of this type. .2 Health and Safety: .1 Do construction occupational health and safety in accordance with Manitoba Workplace Safety and Health Requirements. .3 COR Certification: .1 All member of the design/build team are to be COR Certified to participate in the design, construction or commissioning. |
| 1.12 WASTE MANAGEMENT AND DISPOSAL | .1 Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal. .2 Maintain documentation on total waste in tonnes and the weight of reusable and recycled material in tonnes for submission and achieving the LEED® Credit 2.2 for Materials & Resources: Construction Waste Management – Divert 75% from Landfill. |
| 1.13 WARRANTY | .1 Refer to contractual documents for warranty duration. .2 Refer to individual specification sections for an enhanced warranty period for particular systems if required. |
| 1.14 COMMISSIONING | .1 Submit commissioning plan and copies of testing and commissioning documentation in accordance with Sections 01 91 13 - General Commissioning (Cx) Requirements. |
| 1.15 MATERIALS AND EQUIPMENT | .1 Equipment: .1 CSA approved and ULC certified where applicable. .2 Where CSA or ULC designation is not available, obtain approval from local authority having jurisdiction. .2 Ensure labels are visible and legible after equipment is installed. .3 Factory assemble control panels and component assemblies. |
| 1.16 FINISHES | .1 Shop finish metal enclosure surfaces by application of rust resistant primer inside and outside, and two coats of finish enamel. .1 Paint outdoor electrical equipment "equipment" green finish to EEMAC Y1-1. .2 Paint indoor switchgear and distribution enclosures light grey to EEMAC 2Y-1. .3 Paint recessed and surface panelboard enclosures in non service areas to match wall finish. |
| 1.17 EQUIPMENT IDENTIFICATION | .1 Identify electrical equipment with nameplates. .2 Nameplates: .1 Lamicoid 3 mm thick plastic engraving sheet, black face, white core, mechanically attached with self tapping screws. |

NAMEPLATE SIZES

Size 3		3 mm high letters

Size 5		5 mm high letters

Size 6		6 mm high letters

Size 8		8 mm high letters

Size 10		10 mm high letters

Size 12		12 mm high letters

|  | .3 Wording on nameplates to be approved by Contract Administrator prior to manufacture. .4 Allow for average of twenty-five letters per nameplate. .5 Identification to be English. .6 Nameplates for terminal cabinets and junction boxes to indicate system and/or voltage characteristics. .7 Main distribution and Sub distributions, Size 12: indicate name, system and voltage, calculated fault level, feeder length and size. .8 Disconnects, starters and contactors, Size 8: indicate equipment being controlled voltage and circuit. .9 Terminal cabinets and pull boxes, Size 8: indicate name, system and voltage. .10 Transformers, Size 12: indicate name, capacity, primary and secondary voltages, fed from feeds. .11 Receptacles, Size 3: circuit. |
| --- | --- |
| 1.18 WIRING IDENTIFICATION | .1 Identify wiring with permanent indelible identifying markings, either numbered or coloured plastic tapes, on both ends of phase conductors of feeders and branch circuit wiring. .2 Maintain phase sequence and colour coding throughout. .3 Colour code: to CSA C22.1 .4 Use colour coded wires for fire alarm and communication cables, matched throughout. |
| 1.19 CONDUIT AND CABLE IDENTIFICATION | .1 Colour code conduits, boxes and metallic sheathed cables. .2 Code with paint at points where conduit or cable enters wall, ceiling or floor, and at 15 m intervals. .3 Colours: 25 mm wide prime colour and 20 mm wide auxiliary colour. |

System	Prime		Auxiliary

up to 250 V	Yellow

up to 600 V	Yellow		Green

up to 5 kV	Yellow	 	Blue

up to 15 kV	Yellow		Red

Telecommunication

Systems 	Green

Fire Alarm	Red

Security 	Orange

|  | .4 Provide identification of equipment, components, and assemblies specified, using materials suitable to withstand anticipated operating environment. |
| --- | --- |
| 1.20 FIELD QUALITY CONTROL | .1 Confirm other related work is complete to receive work of this and related electrical sections. .2 Commission electrical systems. .3 Qualifications: .1 Electricians:qualified, licensed electricians or apprentices in accordance with Provincial Act respecting manpower vocational training and qualifications. .2 Apprentices: employees registered in provincial apprentices program permitted, under direct supervision of qualified licensed electrician, to perform specific tasks. Permitted activities determined based on level of training attained and demonstration of ability to perform specific duties. .4 Design-builder holding valid Master Design-builder license as issued by the Province of Manitoba. |
| 1.21 INSTALLATION | .1 Comply with manufacturer's written data, including product technical bulletins, product catalog installation instructions, product carton installation instructions, MSDS, and product datasheets. .2 Protect electrical equipment from dust and dirt. Plug or cap openings in conduit, fixtures and equipment during construction with Contract Administrator approved materials. .3 Set equipment and components plumb and level, accurate to position intended, and position hanger rods plumb. |
| 1.22 HEAVE AND SETTLEMENT | .1 Underground services and supports are to be designed to accommodate heave and settlement which is expected to occur on this Remediated site or the Design Build Team’s site. .2 Provide connections to power door operators as required. |
| 1.23 ACCESSIBLE DESIGN | .1 Installation shall satisfy City of Winnipeg Accessible Design requirements. .2 Provide connections to power door operators as required. |
| 1.24 EQUIPMENT HEIGHTS | .1 City of Winnipeg Accessible Design requirements take precedence over this section. .2 Equipment mounting height, from finished floor to centerline of equipment item: .1 Local switches: 1400 mm. .2 Wall receptacles, general: 300 mm. .3 Receptacles above top of counters or splashback: 175 mm. .4 Receptacle above top of electric baseboard: 200 mm. .5 Receptacles in mechanical rooms: 1400 mm. .6 Panelboards: as required by Code or as indicated. .1 1800 mm from the top of panel to floor. .2 Bottom of panel, minimum 150 mm above floor. .3 Where multiple panelboards are mounted together, align tops or trims of panelboards, with highest panelboard determining height. .7 General telephone, interphone and cable TV outlets: 300 mm. .8 Wall mounted telephone and interphone: 1400 mm. .9 Fire alarm stations: 1400 mm. .10 Wall mounted fire alarm, horns, wall mounted speakers and clocks: 2100 mm. .11 Emergency lighting battery units: 2400 mm. .12 Wall mounted dry type transformers: 2400 mm from bottom. .13 Time switches: 1400 mm. .14 Individual starters: 1500 mm from top. Where multiple starters are mounted together, align starter tops with highest starter determining height. .3 Attach electrical equipment, components and devices directly to structure and structural supporting elements. |
| 1.25 MANUFACTURER'S SERVICES | .1 Engage manufacturer's representative to review work, installation or application of products, protection required, and final product cleaning. .1 Submit written reports to Design Build Team Engineer and Contract Administrator to verify compliance with project requirements. .2 Provide manufacturer's field services consisting of product use recommendations and periodic site visits for inspection of product installation in accordance with manufacturer's instructions. .3 Schedule manufacturer site visits to review work, at following stages as minimum: .1 After delivery and storage of products, when preparation is complete, but prior to installation. .2 Twice during equipment installation. .3 Upon completion of Work, after cleaning is complete. .4 Obtain manufacturer's review reports within 3 days of review, and submit to Design Build Team Engineer and Contract Administrator. |
| 1.26 VERIFICATION | .1 Measure phase current to panelboards with normal loads operating at time of acceptance. Adjust branch circuit connections as required to obtain best balance of current between phases and record changes. .2 Measure phase voltages at loads and adjust transformer taps to within 2% of rated voltage of equipment. .3 Submit report, at completion of measurements, listing phase and neutral currents on panelboards, dry-type transformers and motor control centres, operating under normal load. Include hour and date on which load was measured, and voltage at time of test. |
| 1.27 FIELD TESTS | .1 Provide advance notice to Design Build Team Engineer and Contract Administrator of proposed testing schedule. .2 Perform tests at time of acceptance of work. .3 Conduct and pay for field tests: .1 Power distribution, including phase voltage, grounding and load balancing. .2 Circuits originating from branch distribution panels. .3 Lighting and lighting control. .4 Motors, heaters and associated control equipment, including sequenced operation. .5 Fire alarm and communications (and their interface) systems. .6 Telecommunications cabling. .4 Perform tests in presence of Design Build Team Engineer and Contract Administrator. .1 Provide instruments, meters, equipment and personnel required to conduct required tests. .2 Test systems to verify operation as specified. .5 Conduct di-electric tests, hi-pot tests, ground resistance tests, insulation resistance tests and ground continuity tests as required by nature of various systems and equipment. .6 Perform following tests on completed power systems: .1 Control and switching: test circuits for correct operation of devices, switches and controls. .2 Polarity tests: test circuits for correct operation of devices, switches and controls. .3 Voltage tests: test voltage at last outlet of each circuit; maximum potential drop 2% on 120 V, and 208 V branch circuits, 2% on 208 V feeder circuits, and 5% on 600 V feeder circuits. Correct deficiencies. .4 Phase balance: measure load on each phase at switchboards, splitter, distribution panel board and lighting and power panel board. .1 Submit results to Design Build Team Engineer in writing. .2 Re-arrange phase connections as necessary to balance load on each phase as instructed by Design Build Team Engineer. .3 After marking such changes, submit revised drawings showing modified connections to Design Build Team Engineer. .5 Supply voltage: measure line voltage of each phase at load terminals of main breakers and report results in writing to Design Build Team Engineer. Perform test with majority of electrical equipment in use. .6 Motor loading: measure line current of each phase of motors with motor operating under load, and report results in writing to Design Build Team Engineer. .1 Upon indications of imbalances or overloads, thoroughly examine electrical connections and rectify defective parts or wiring. .2 If electrical connections are correct, report overloads due to defects in driven machines in writing to Design Build Team Engineer. .7 Insulation resistance tests: .1 Megger circuits, feeders and equipment up to 350 V with a 500 V instrument. .2 Megger 350-600 V circuits, feeders and equipment with a 1000 V instrument. .3 Check resistance to ground before energizing. .8 Co-ordinate and carry out motor testing at same time as driven equipment is being tested. In addition to motor loading tests, provide labour and instruments to read and record motor load readings required to supplement tests on driven equipment through various load sequences, as required by driven equipment tests. .7 General operations: energize and operate electrical circuit and item. Repair, alter, replace, test and adjust as necessary for a complete and operating electrical system. .8 Test systems and obtain written confirmation from manufacturers that components have been installed correctly and system functioning as intended. Submit certification for fire alarm, power distribution, communications systems, and security systems integrator. .9 Provide labour, instruments, apparatus and pay expenses required for testing. Design Build Team Engineer and Contract Administrator reserves right to demand proof of accuracy of instruments used. .10 Immediately prior to occupancy, test entire electrical system by performing loss and return of utility power test. Demonstrate operation of: .1 Low voltage service equipment and metering. .2 Exit and emergency lighting. .3 Fire and intrusion alarm operation during power outage, including remote monitoring system. .4 Access control and intrusion detection. .5 CCTV system. .6 System shut down and auto restart, including restabilization of systems after power return. .7 User equipment shut-down and auto-restart. .8 Attach report printouts as evidence of expected operation on systems. |
| 1.28 TEST RESULTS | .1 Submit test results to Design Build Team Engineer and Contract Administrator for review. .2 Testing methods and test results: to CSA, CEC and authorities having jurisdiction. .3 Remove and replace conductors found damaged, with new materials. .4 Provide required labour and tools, if during testing Design Build Team Engineer requests equipment be opened and removed from their housings to examine equipment, terminations and connections. |
| 1.29 TRAINING | .1 Train operating personnel in operation, care and maintenance of electrical equipment. .2 Arrange and pay for manufacturer's factory service engineer to provide training. Ensure operating personnel are conversant with its care and operation. .3 Obtain and submit written confirmation from operating personnel that satisfactory training has been received. .4 Provide one day training session for following systems. .1 Fire Alarm. .2 Card access and Intrusion system. .3 Telecommunication systems. .5 Electrical distribution, control & instrumentation. |
| 1.30 CLEANING | .1 Perform final cleaning of electrical equipment, systems and components. |
| 1.31 PRODUCT STANDARDS | .1 Where products are indicated, the following definitions apply: .1 Acceptable manufacturers: only products supplied by the indicated manufacturers are to be provided. .2 Standard of acceptance: the listed product or manufacturer provides the required features. Alternate manufacturers can be utilized provided they also provide the same features as the listed product or manufacturer. The Design Build Team may be asked to submit proof that the alternate product meets the standard of acceptance. |
| PART 2 - PRODUCTS |  |
| 2.1 SUSTAINABLE REQUIREMENTS | .1 Use only low emitting adhesives, caulking, paint, coatings and sealants to meet LEED® Credits 4.1 and 4.2 under Indoor Environmental Quality: Low Emitting Materials. |
| 2.2 SPRINKLER PROOF | .1 All major electrical equipment are to be sprinkler proof. This shall include but not be limited to: .1 Main distribution, sub-distribution and surface mounted panelboards. .2 Transformers. .3 Motor control centres and discrete starters. .2 Top entry shall utilize waterproof connectors. |
| PART 3 - EXECUTION |  |
| 3.1 FIELD QUALITY CONTROL | .1 Verification requirements in accordance with Section 01 47 17 - Sustainable Requirements: Design Build Team's Verification, include: .1 Materials and resources. .2 Storage and collection of recyclables. .3 Construction waste management. .4 Resource reuse. .5 Recycled content. .6 Local/regional materials. .7 Low-emitting materials. |
| 3.2 CLEANING | .1 Proceed in accordance with Section 01 74 11 - Cleaning. .2 Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment. |