| PART 1 - GENERAL |  |
| --- | --- |
| 1.1 SUMMARY | .1 This Section outlines requirements for supply and installation of land drainage sewers, catch basins, manholes, fittings, and appurtenances, and connections to existing catch basins, manholes, and sewers. |
| 1.2 REFERENCES AND RELATED SECTIONS | .1 City of Winnipeg Standard Construction Specifications: .1 CW 2130 – Gravity Sewers. .2 City of Winnipeg Standards and Guidelines for the Mitigation of Methane Gas at Buildings and Utilities and Guidelines for Construction on Landfill Sites. .3 Related Sections: .1 01 33 00 - Submittal Procedures. .2 01 74 19 – Construction Waste Management And Disposal. .3 31 23 33.01 - Excavating, Trenching and Backfilling. .4 Canada Green Building Council (CaGBC) LEED® Green Building Rating System – LEED® Canada-NC Version 1.0. |
| 1.3 PERFORMANCE REQUIREMENTS | .1 Work shall be performed in accordance with CW 2130 – Gravity Sewers, and Section 31 23 33.01 – Excavating, Trenching and Backfilling. .2 The design shall include methods and specifications intended to achieve acceptable performance as the site settles, and help minimize future maintenance requirements. .3 The design shall consider the chemical and physical effects of fill materials present at the site on the integrity of the building and services. .4 In order to minimize the potential for underground gas migration within excavations and trenches, buried municipal services shall be installed in a common trench system wherever possible. .5 Locate sewer mains, manholes, catchbasins, catchpits, valves, gates, culverts, and appurtenances to minimize the impact of trench settlement on surface features. .6 Minimize the number of offsite land drainage system connections to: .1 Reduce the impact of service interruptions to existing areas and users. .2 Minimize the requirement for installation of gas barriers and trench gas migration plugs. .7 Service connections to buildings shall be constructed such that: .1 Differential settlement between the service and the structural slab floor does not negatively impact the integrity, operation or performance of the utility. .2 Any utility or conduit entering through the floor shall be sealed to prevent infiltration of methane gas into the building. .8 The land drainage system (LDS) shall be designed in such a way that failure of the LDS piping system to handle a storm of greater intensity than the design storm should not result in property damage due to runoff. .9 A double backflow prevention system shall be employed on the downstream end of the LDS system. The backflow preventors shall consist of two flap-gate structures installed to prevent backflow of wastewater from the combined sewer system into the stormwater pond. .10 The inlet structure upstream of the combined sewer connection shall be a 375 mm diameter restricted inlet system. .11 The LDS pipe section downstream of the inlet structure shall be maximum 375 mm diameter. |
| 1.4 SUBMITTALS | .1 Submit designs, shop drawings, plans and details in accordance with Section 01 33 00 - Submittal Procedures. .2 Prior to beginning excavation submit for approval by the Contract Administrator, plans, drawings and documentation in support of: .1 Plan/profile drawings clearly indicating pipe alignments, depth, grades, pipe size, class, material, and any other information pertinent to the design of the land drainage piping system. .2 Indicate trench/excavation type (i.e. open-cut, trenchless), bedding classes, and location of trench gas barriers. .3 Design and detail drawings for land drainage system appurtenances, including building service connection details. .3 Testing, laboratory results, and quality control documentation shall be made available to the Contract Administrator upon request. |
| 1.5 QUALITY ASSURANCE | .1 Sustainable Requirements: .1 Design Build Team shall perform work in accordance with: .1 Section 01 47 13 – LEED Requirements. .2 Section 01 74 19 – Construction Waste Management and Disposal. |
| 1.6 DELIVERY, STORAGE AND HANDLING | .1 Storage and Protection: .1 Prevent damage to fencing, trees, landscaping, natural features, benchmarks, existing buildings, existing pavement, utility lines, site appurtenances, water courses, and root systems of trees which are to remain. .2 Protect benchmarks, property corners, and other survey monuments from damage or displacement. If marker needs to be removed, reference and replaced it by licensed land surveyor at the contractor’s expense. .3 Temporarily cover catch basins and maintenance holes to prevent entry of earth, debris, construction materials, or other deleterious substances. Ensure adequate surface drainage in affected area is maintained. .4 Provide traffic control as required, in accordance with applicable regulations. |
| PART 2 - PRODUCTS |  |
| 2.1 MATERIALS | .1 Materials and products in accordance with CW 2130 – Gravity Sewers. .2 The inlet structure upstream of the combined sewer connection shall be a 150mm diameter restricted inlet system (Hickenbottom, Inc., or approved equal). |
| PART 3 - EXECUTION |  |
| 3.1 PREPARATION | .1 Clean pipes and fittings of debris and water before installation. .2 Handle defective materials, off-cuts, packaging, crating, extra materials, and debris in accordance with the Waste Management Plan (WMP). |
| 3.2 INSTALLATION | .1 Do trenching Work in accordance with Section 31 23 33.01 - Excavating, Trenching and Backfilling. .2 Do not allow contents of sewer or sewer connection to flow into trench. |
| 3.3 BACKFILL | .1 Backfill methods and materials as per Section 31 23 33.01 – Excavating, Trenching and Backfilling. |
| 3.4 RESTORATION | .1 Restorations shall be performed in accordance with CW 2130 – Gravity Sewers. |