## Sheet1
Process Code | Process Description | Sample Commodity | Sample Location Description | Sample Equipment | Sample Collection Description | Analytical Parameters | Minimum Monitoring Frequency | Primary Purpose
N | Hauled Sludge Receiving | Hauled Sludge | Downstream of each hauled sludge equalization tank | Sample Station | Easy access for sampling. Potable water and sink provided for flushing of sampling lines. | TS | Daily | Process Control
[6 empty] | VS | Daily | Process Control
[6 empty] | Ammonia | 2/Week | Monitoring
[6 empty] | TKN | 2/Week | Monitoring
[6 empty] | Ortho P | 3/Week | Process Control
[6 empty] | TP | 3/Week | Process Control
[6 empty] | VFA Total | 3/Week | Process Control
[6 empty] | VFA (acetic and propionic) | Monthly | Monitoring
[6 empty] | pH | 3/Week | Monitoring
J | Phosphorus Release | Hauled Sludge | Upstream of each phosphorus release tank | Sampling Port | Easy access for sampling. | TS | Weekly | Monitoring
[6 empty] | VS | Weekly | Monitoring
[6 empty] | pH | Weekly | Monitoring
[6 empty] | Ammonia | Weekly | Monitoring
[6 empty] | TKN | Weekly | Monitoring
[6 empty] | TP | Weekly | Monitoring
[6 empty] | Ortho P | Weekly | Monitoring
[6 empty] | VFA Total | Weekly | Monitoring
J | Phosphorus Release | Phosphorus Released Sludge | Downstream of each phosphorus release tank | Sample Station | Easy access for sampling. Potable water and sink provided for flushing of sampling lines. | TS | Daily | Monitoring
[6 empty] | VS | Daily | Process Control
[6 empty] | pH | Daily | Monitoring
[6 empty] | Temperature | Daily | Monitoring
[6 empty] | Ammonia | 2/Week | Monitoring
[6 empty] | TKN | 2/Week | Monitoring
[6 empty] | TP | Daily | Process Control
[6 empty] | Ortho P | Daily | Process Control
[6 empty] | VFA Total | 2/Week | Process Control
[5 empty] | Analysis conducted on-site using moisture analyzer. | TS | 2/ Day | Process Control
T | Pre-digestion Sludge Treatment: Sludge Screening | Primary Sludge | Upstream of the primary sludge screens | Sample Station | Easy access for sampling. Potable water and sink provided for flushing of sampling lines. | TS | Daily | Process Control
[6 empty] | VS | Daily | Process Control
[6 empty] | TKN | As required | Monitoring
[6 empty] | TP | As required | Monitoring
[6 empty] | VFA Total | 2/Week | Monitoring
T | Pre-digestion Sludge Treatment: Sludge Screening | Screened Sludge | From each sludge screen | Sampling Port | Easy access for sampling. | TS | As required | Removal Efficiencies
[6 empty] | VS | As required | Removal Efficiencies
T | Pre-digestion Sludge Treatment: Sludge Screening | Screenings | From each sludge screenings bin | By Hand | Easy access for sampling. | TS | As required | Monitoring
[6 empty] | Concrete Slump Test | As required | Landfill Licence
T | Pre-digestion Sludge Treatment: Sludge Screening | Screened Sludge | Downstream of each screened sludge equalization tank | Sample Station | Easy access for sampling. Potable water and sink provided for flushing of sampling lines. | TS | Daily | Process Control/Removal Efficiencies
[6 empty] | VS | Daily | Process Control/Removal Efficiencies
[6 empty] | pH | Daily | Monitoring
[6 empty] | Temperature | Daily | Monitoring
[6 empty] | Ammonia | 2/Week | Monitoring
[6 empty] | TKN | 2/Week | Monitoring
[6 empty] | TP | 2/Week | Monitoring
[6 empty] | Ortho P | 2/Week | Monitoring
[6 empty] | VFA Total | Weekly | Monitoring
T | Pre-digestion Sludge Treatment: Intermediate Dewatering | Dewatered Sludge | From each intermediate centrifuge | Sample Station | Easy access for sampling. Potable water and sink provided for flushing of sampling lines. | TS | Daily | Process Control
[6 empty] | VS | Daily | Process Control
[6 empty] | TKN | 2/Week | Monitoring
[6 empty] | TP | 2/Week | Monitoring
T | Pre-digestion Sludge Treatment: Intermediate Dewatering | Mixed Polymer | From each polymer make-up system | Sampling Port | Easy access for sampling. | TS | As required | Product Check
T | Pre-digestion Sludge Treatment: Intermediate Dewatering | Dewatered Sludge | Downstream of each intermediate dewatered sludge hoppers | Sample Station | Easy access for sampling. Potable water and sink provided for flushing of sampling lines. | TS | Daily | Monitoring
[6 empty] | VS | Daily | Process Control
[6 empty] | Temperature | Daily | Monitoring
[5 empty] | Analysis conducted on-site using moisture analyzer. | TS | 2/ Day | Process Control
T | Pre-digestion Sludge Treatment: Thermal Hydrolysis | Design Builder shall meet THP sampling requirements as per Schedule 18V - Cambi Contract Documents.
T | Pre-digestion Sludge Treatment: Thermal Hydrolysis | Conditioned Sludge | Downstream of each THP train | Sample Station | Easy access for sampling. Potable water and sink provided for flushing of sampling lines. | TS | Daily | Process Control
[6 empty] | VS | Daily | Process Control
[6 empty] | Temperature | Daily | Monitoring
[6 empty] | Ammonia | 2/Week | Monitoring
[6 empty] | TKN | 2/Week | Monitoring
[6 empty] | TP | 2/Week | Monitoring
[6 empty] | Ortho P | 2/Week | Monitoring
D | Anaerobic Digestion: Anaerobic Digesters | Liquid Biosolids | Upstream of each digester | Sampling Port | Easy access for sampling. | TS | As required | Monitoring
[6 empty] | VS | As required | Monitoring
[6 empty] | pH | As required | Monitoring
[6 empty] | Temperature | As required | Monitoring
[6 empty] | Ammonia | As required | Monitoring
[6 empty] | TKN | As required | Monitoring
[6 empty] | TP | As required | Monitoring
[6 empty] | Ortho P | As required | Monitoring
D | Anaerobic Digestion: Anaerobic Digesters | Liquid Biosolids | Downstream of each digester | Sample Station | Easy access for sampling. Potable water and sink provided for flushing of sampling lines. | TS | Daily | Process Control
[6 empty] | VS | Daily | Process Control
[6 empty] | pH | Daily | Process Control
[6 empty] | Temperature | Daily | Process Control
[6 empty] | Ammonia | 2/Week | Monitoring
[6 empty] | TKN | 2/Week | Monitoring
[6 empty] | TP | 2/Week | Monitoring
[6 empty] | Ortho P | 2/Week | Monitoring
[6 empty] | Gas Analysis (CH4 & H2S) | 2/Week | Monitoring
D | Anaerobic Digestion: Anaerobic Digesters | Digester Gas | From each digester | Sampling Port | Easy access for sampling. | H2S | Monthly | Process Control/Removal Efficiencies
[6 empty] | CO2 | Monthly | Monitoring
[6 empty] | CH4 | Monthly | Monitoring
[6 empty] | N2 | Monthly | Monitoring
D | Anaerobic Digestion: Biosolids Holding | Liquid Biosolids | Downstream of each biosolids holding tank | Sample Station | Easy access for sampling. Potable water and sink provided for flushing of sampling lines. | TS | 2/Week | Monitoring
[6 empty] | VS | 2/Week | Monitoring
[6 empty] | pH | 2/Week | Monitoring
[6 empty] | Temperature | 2/Week | Monitoring
[6 empty] | Ammonia | 2/Week | Monitoring
[6 empty] | TKN | 2/Week | Monitoring
[6 empty] | TP | 2/Week | Monitoring
[6 empty] | Ortho P | 2/Week | Monitoring
[6 empty] | Gas Analysis (CH4 & H2S) | 2/Week | Monitoring
V | Biosolids Processing and Loading: Final Dewatering | Dewatered Biosolids | From each final centrifuge | Sample Station | Easy access for sampling. Potable water and sink provided for flushing of sampling lines. | TS | Daily | Process Control
[6 empty] | VS | Daily | Process Control
[6 empty] | TKN | 2/Week | Monitoring
[6 empty] | TP | 2/Week | Monitoring
V | Biosolids Processing and Loading: Final Dewatering | Mixed Polymer | From each polymer make-up system | Sampling Port | Easy access for sampling. | TS | As required | Product Check
V | Biosolids Processing and Loading: Phosphorus Recovery | Intermediate Centrate | Upstream of the phosphorus recovery reactors | Sampling Port | Easy access for sampling. | Alkalinity | Daily | Process Control
[6 empty] | pH | Daily | Process Control
[6 empty] | Ammonia | Daily | Process Control/Removal Efficiencies
[6 empty] | TKN | Daily | Process Control/Removal Efficiencies
[6 empty] | Ortho P | Daily | Process Control/Removal Efficiencies
[6 empty] | TP | Daily | Process Control/Removal Efficiencies
[6 empty] | TSS | Daily | Monitoring
[6 empty] | VSS | Daily | Monitoring
[6 empty] | Magnesium - Dissolved | Monthly | Monitoring
[6 empty] | Calcium - Dissolved | Monthly | Monitoring
V | Biosolids Processing and Loading: Phosphorus Recovery | Final Centrate | Upstream of the phosphorus recovery reactors | Sampling Port | Easy access for sampling. | Alkalinity | Daily | Process Control
[6 empty] | pH | Daily | Process Control
[6 empty] | Ammonia | Daily | Process Control/Removal Efficiencies
[6 empty] | TKN | Daily | Process Control/Removal Efficiencies
[6 empty] | Ortho P | Daily | Process Control/Removal Efficiencies
[6 empty] | TP | Daily | Process Control/Removal Efficiencies
[6 empty] | TSS | Daily | Monitoring
[6 empty] | VSS | Daily | Monitoring
[6 empty] | Magnesium - Dissolved | Monthly | Monitoring
[6 empty] | Calcium - Dissolved | Monthly | Monitoring
V | Biosolids Processing and Loading: Phosphorus Recovery | Phosphorus Recovery Effluent | Downstream of each phosphorus recovery reactor | Automatic Composite Sampler | Automatic, plunger sampler mounted in mid section of pressurized pipe with carboy in refrigerator for sample storage. Programmed to collect flow-weighted samples. Provide means to minimize impact of biofilm growth on quality of samples. Ensure that all automatic samplers are designed to meet the area classification. | Alkalinity | Daily | Process Control
[6 empty] | pH | Daily | Process Control
[6 empty] | Ammonia | Daily | Process Control
[6 empty] | TKN | Daily | Process Control
[6 empty] | TN | Daily | Regulatory
[6 empty] | Ortho P | Daily | Process Control
[6 empty] | TP | Daily | Process Control
[6 empty] | TSS | Daily | Process Control
[6 empty] | VSS | Daily | Process Control
[6 empty] | BOD - Total | Daily | Process Control
[6 empty] | BOD - Carbonaceous | Daily | Process Control
[6 empty] | BOD - Soluble Carbonaceous | Daily | Process Control
[6 empty] | COD - Total | Daily | Process Control
[6 empty] | COD - Soluble | Daily | Process Control
[6 empty] | SOUR | As required | Process Control
V | Biosolids Processing and Loading: Phosphorus Recovery | Design Builder shall meet the phosphorus recovery process sampling requirements as per Schedule 18W - Ostara Contract Documents.
K | Digester Gas Handling: Digester Gas Storage | Digester Gas | From each digester gas storage sphere | Sampling Port | Easy access for sampling. | H2S | Monthly | Process Control/Removal Efficiencies
[6 empty] | CO2 | Monthly | Monitoring
[6 empty] | CH4 | Monthly | Monitoring
[6 empty] | N2 | Monthly | Monitoring
K | Digester Gas Handling: Digester Gas Flare Stacks | Digester Gas | At each flare prior to combustion | Sampling Port | Easy access for sampling. | H2S | Quarterly | Process Control/Removal Efficiencies
[6 empty] | CO2 | Quarterly | Monitoring
[6 empty] | CH4 | Quarterly | Monitoring
[6 empty] | N2 | Quarterly | Monitoring
[6 empty] | Humidity | Quarterly | Monitoring
K | Digester Gas Handling: H2S Removal | Digester Gas | From each H2S removal vessel | Sampling Port | Easy access for sampling. | H2S | Quarterly | On-line instrument Check
|  |  |  | On-line Instrument | Easy access for calibration and maintenance. Ensure that all automatic samplers are designed to meet the area classification. | H2S | Continuous | Process Control/Removal Efficiencies
K | Digester Gas Handling: Digester Gas Conditioning | Conditioned Digester Gas | From each digester gas conditioning unit | Sampling Port | Easy access for sampling. | H2S | Quarterly | Process Control/Removal Efficiencies
[6 empty] | CO2 | Quarterly | Monitoring
[6 empty] | CH4 | Quarterly | Monitoring
[6 empty] | N2 | Quarterly | Monitoring
[6 empty] | Humidity | Quarterly | Monitoring
| Return Lift Station | Raw Sewage | From the return lift station | Automatic Composite Sampler | Automatic, plunger sampler mounted in mid section of pressurized pipe with carboy in refrigerator for sample storage. Programmed to collect flow-weighted samples. Provide means to minimize impact of biofilm growth on quality of samples. Ensure that all automatic samplers are designed to meet the area classification. | Alkalinity | Daily | Source Control
[6 empty] | pH | Daily | Source Control
[6 empty] | Temperature | Daily | Source Control
[6 empty] | Ammonia | Daily | Source Control
[6 empty] | Nitrite | Daily | Source Control
[6 empty] | Nitrate | Daily | Source Control
[6 empty] | TKN | Daily | Source Control
[6 empty] | TN | Daily | Source Control
[6 empty] | Ortho P | Daily | Source Control
[6 empty] | TP | Daily | Source Control
[6 empty] | TSS | Daily | Source Control
[6 empty] | VSS | Daily | Source Control
[6 empty] | BOD - Total | Daily | Source Control
[6 empty] | BOD - Carbonaceous | Daily | Source Control
[6 empty] | BOD - Soluble Carbonaceous | Daily | Source Control
[6 empty] | COD - Total | Daily | Source Control
[6 empty] | COD - Soluble | Daily | Source Control
T | Pre-digestion Sludge Treatment: Thermal Hydrolysis | Flushing Water (for THP dilution) | Upstream of each THP train | Sampling Port | Easy access for sampling. | Alkalinity | Daily | Monitoring
[6 empty] | pH | Daily | Monitoring
[6 empty] | Temperature | Daily | Monitoring
[6 empty] | Total Residual Chlorine (TRC) | Daily | Process Control
[6 empty] | Ammonia | Daily | Monitoring
[6 empty] | TDS | Daily | Monitoring
[6 empty] | E. Coli & Fecal Coliform | Daily | Monitoring
|  |  |  | On-line Instrument | Easy access for calibration and maintenance. | Conductivity | Continuous | Monitoring
T | Pre-Digestion Sludge Treatment: Odour Control | Foul Air | Upstream of each odour control system | Sampling Port | Easy access for sampling. Sampling port opening to allow direct sampling from air stream with space for a 15 mm tube. | H2S | As required | Monitoring
V | Biosolids Processing & Loading: Odour Control
T | Pre-Digestion Sludge Treatment: Odour Control | Foul Air | Upstream of each odour control system | On-line Instrument | Easy access for calibration and maintenance. | H2S | Continuous | Monitoring
V | Biosolids Processing & Loading: Odour Control
T | Pre-Digestion Sludge Treatment: Odour Control | Foul Air | Downstream of each odour control system (prior to release to atmosphere) | Sampling Port | Easy access for sampling. Sampling port opening to allow direct sampling from air stream with space for a 15 mm tube. | H2S | Weekly | Monitoring
V | Biosolids Processing & Loading: Odour Control
T | Pre-Digestion Sludge Treatment: Odour Control | Foul Air | Downstream of each odour control system (prior to release to atmosphere) | On-line Instrument | Easy access for calibration and maintenance. | H2S | Continuous | Monitoring
V | Biosolids Processing & Loading: Odour Control
N J T V | Hauled Sludge Receiving Phosphorus Release Pre-Digestion Sludge Treatment Biosolids Processing & Loading | Foul Air | Foul air at the following locations: (a) ; (b) phosphorus release tanks; (c) sludge screenings bins; (d) waste activated sludge thickeners; (e) thickened sludge tanks; (f) intermediate centrate tanks; (g) screened sludge equalization tanks; (h) intermediate dewatering centrifuges; (i) dewatered sludge hoppers; (j) dewatered sludge chutes; (k) sludge receiving station; (l) hauled sludge equalization tanks; (m) final dewatering centrifuges; (n) final dewatering centrate tanks; (o) biosolids storage hoppers; (p) biosolids truck loading chutes; and (q) phosphorus recovery reactor. | Sampling Port | Easy access for sampling. Sampling port opening to allow direct sampling from air stream with space for a 15 mm tube. | H2S | As required | Monitoring
[6 empty] | CO2 | As required | Monitoring
[6 empty] | CH4 | As required | Monitoring
[6 empty] | N2 | As required | Monitoring