## ASSET CLASSIFICATION BREAKDOWN
BUILDING
Parent | Building General
Parent | Motor Room 1-Ton Monorail
Parent | Main Floor 2-Ton Monorail
CONTROL PANELS
Parent | PLC Control Panel CP-L81
Child | PLC Rack PLC-L81
Child | Uninteruptible Power Supply UPS-L81
Parent | HVAC Control Panel JBA-L86
ELECTRICAL EQUIPMENT
Parent | Automatic Transfer Switch ATS-L72
Parent | Customer Service Term End CSTE-L70
Parent | Emergency Lighting ELB-L74
Parent | Standby Generator GEN-L72
Parent | Emergency Motor Control Center MCC-L72E
Parent | Distribution Panelboard PNL-L73E
Parent | Main Switchgear SGR-L71
Parent | Surge Suppressor TVSS-L71
Parent | Variable Frequency Drive VFD-L01
Parent | Variable Frequency Drive VFD-L02
Parent | Variable Frequency Drive VFD-L03
Parent | Transformer XFMR-L73E
HVAC
Parent | Outdoor Air Conditioner AHU-L65
Parent | Vent. Supply Damper Actuator FV-L621
Parent | Vent. Return Damper Actuator FV-L622
Parent | Vent. Exhaust Damper Actuator FV-L623
Parent | Ventilation Duct Heater HCE-L63
Parent | Ventilation Supply Fan SF-L62
Parent | Gen. Supply Damper Actuator TV-L662-A
Parent | Gen. Supply Damper Actuator TV-L662-B
Parent | Gen. Return Damper Actuator TV-L663
Parent | Gen. Exhaust Damper Actuator TV-L664
Parent | Main Floor Unit Heater UH-L64
Parent | Gen. Combustion Damper Actuator XV-L661
Parent | Miscellaneous Duct Work
INSTRUMENTS
Parent | Generator Gas Detector AIT-L550
Parent | Pump P-L01 Flow Transmitter FIT-L011
Parent | Pump P-L02 Flow Transmitter FIT-L021
Parent | Pump P-L03 Flow Transmitter FIT-L031
Parent | Pump P-L01 Seal Water Flow FSL-L012
Parent | Pump P-L02 Seal Water Flow FSL-L022
Parent | Pump P-L03 Seal Water Flow FSL-L032
Parent | Wet Well Level Controller LIC-L500
Parent | Wet Well Level Transmitter LIT-L500-A
Parent | Wet Well Level Transmitter LIT-L500-B
Parent | Differential Pressure Switch PDSH-L611
Parent | Generator Temp Controller TIC-L660
Parent | Main Floor Temp Transmitter TT-L601
Parent | HVAC Temp. Controller UIC-L600
Parent | Pump P-L01 Seal Water Valve YV-L012
Parent | Pump P-L02 Seal Water Valve YV-L022
Parent | Pump P-L03 Seal Water Valve YV-L032
MOTORS
Parent | Lift Pump Motor MTR-L01
Parent | Lift Pump Motor MTR-L02
Parent | Lift Pump Motor MTR-L03
PROCESS PIPING & VALVES
Parent | P-L01 Check Valve CV-L01
Parent | P-L02 Check Valve CV-L02
Parent | P-L03 Check Valve CV-L03
Parent | P-L01 Discharge Valve DV-P-L01
Parent | P-L02 Discharge Valve DV-P-L02
Parent | P-L03 Discharge Valve DV-P-L03
Parent | P-L01 Upstream Iso Valve UIV-P-L01
Parent | P-L02 Upstream Iso Valve UIV-P-L02
Parent | P-L03 Upstream Iso Valve UIV-P-L03
Parent | Lift Pump P-L01 Sanitary Piping
Parent | Lift Pump P-L02 Sanitary Piping
Parent | Lift Pump P-L03 Sanitary Piping
Parent | Potable Water Piping
PUMPS
Parent | Lift Pump P-L01
Parent | Lift Pump P-L02
Parent | Lift Pump P-L03
Parent | Pump Room Sump Pump P-L12

## Building
Asset Type: | Building
Asset Type Code: | WW-BLDG
Asset Data Record | [12 empty] | Specification Data
ASSET HIERARCHY LEVEL | RELATIONSHIP | ASSET_NO - Asset Number | TAGGED - Asset Tag/Name Plate | TAG ID - Tag ID | ASSET_RECORD_TYPE - Asset Record Type | ASSET_DESC - Asset Description | ASSET_STATUS - Asset Status | DEPARTMENT - Administrative Department | AREA - Administrative Area | CRITICALITY - Asset Criticality Rating | BUILDING - Building Number | ROOM - Room (location) | MANUFACTURER - Manufacturer | MAKE - Make | MODEL_NO - Model | SERIAL_NO - Serial Number | CERTIF - Certification (CSA, UL, FM, Class, Div, Grp, Haz/Non-Haz) | Attachment File Name to be Added to Asset
Parent | - |  | No | - | B | Building General | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | All | - | - | - | - | - | -
Parent | - |  | Yes | - | E | Motor Room 1-Ton Monorail | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Motor Room | Vital | Westward | Manual Plain Trolley APD | 1401 | - | 1-Ton Monorail
Parent | - |  | Yes | - | E | Main Floor 2-Ton Monorail | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | - | Morris | - | 10359 | - | 2-Ton Monorail
Note on B4: ASSET HIERARCHY LEVEL: Indicate whether parent asset, child asset, or component.
Note on C4: RELATIONSHIP: If child asset or component, indicate of which parent asset using the tag ID of the parent asset.
Note on D4: ASSET_NO: Synergen Asset ID given at time of hierarchy structure if migrated. Synergen generated if Asset data entered manually.
Note on E4: TAGGED: Use Validation drop down list to select appropriate value. Does the Asset have a Tag ID lamacoid?
Note on F4: ATTRIBUTE1: Smart numbered Tag_ID using City of Winnipeg standard format.
Note on G4: ASSET_RECORD_TYPE: Use Validation drop down list to select appropriate Asset Type. E = Equipment B = Building A = Virtual (used in Asset Hierarchy Structure)
Note on H4: ASSET_DESC: Asset Description Format: -Wastewater Process Area or Water Pumping or Collection Station -Type (HVAC, electrical, sump, clarifier, RAS etc.) -Tag_ID - Common Name (This is what everyone calls it) - Maximum data length = 2000 characters
Note on I4: ASSET_STATUS: Use Validation drop down list to select appropriate Asset Status. Format: Assets in service = ACTIVE
Note on J4: DEPARTMENT: Use Validation drop down list to select appropriate Department. (WWD)
Note on K4: AREA: Use Validation drop down list to select appropriate Area. (Water or Waste)
Note on L4: CRITICALITY: Use Validation drop down. Default the value = 6.
Note on M4: BUILDING: Use Validation drop down list to select appropriate Building. If no appropriate Building is listed provide proposed new Building to City of Winnipeg for consideration.
Note on N4: ROOM: Chlorine, Pump, Control, Motor etc. Name of room where the Asset is located. Maximum data length = 20 characters

## Control Panels
Asset Type: | Control Panels
Asset Type Code: | WW-CONTROL PANELS
Asset Data Record | [12 empty] | Specification Data
ASSET HIERARCHY LEVEL | RELATIONSHIP | ASSET_NO - Asset Number | TAGGED - Asset Tag/Name Plate | TAG ID - Tag ID | ASSET_RECORD_TYPE - Asset Record Type | ASSET_DESC - Asset Description | ASSET_STATUS - Asset Status | DEPARTMENT - Administrative Department | AREA - Administrative Area | CRITICALITY - Asset Criticality Rating | BUILDING - Building Number | ROOM - Room (location) | MANUFACTURER - Manufacturer | MAKE - Make | MODEL_NO - Model | SERIAL_NO - Serial Number | DATEMFR - Date of Manufacture | VOLT - Rated Voltage (V) | AMP - Rated Current (A) | FREQ - Frequency (Hz) | PHASE - Number of Phases | CERTIF - Certification (CSA, UL, FM, Class, Div, Grp, Haz/Non-Haz) | ENCL_PROT - Enclosure Protection Code (NEMA/IP rating) | Attachment File Name to be Added to Asset
Parent | - |  | Yes | CP-L81 | E | PLC Control Panel CP-L81 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | Hoffman | - | A726010ULP | 17306 | - | 120 | 10 | 60 | 1 | CSA | NEMA 12 | CP-L81
Child | CP-L81 |  | Yes | PLC-L81 | E | PLC Rack PLC-L81 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | Schneider Electric | Modicon | M580 | - | - | - | - | - | - | - | - | PLC-L81
Child | CP-L81 |  | Yes | UPS-L81 | E | Uninteruptible Power Supply UPS-L81 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | Phoenix Contact | Quint Series | QUINT-UPS/24DC/24DC/10/3.4AH | 3016221664 | 17/2021 | 24 | 10 | - | - | cUL | - | UPS-L81
Parent | - |  | Yes | JBA-L86 | E | HVAC Control Panel JBA-L86 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | Hoffman | - | A302006LP | 17341 | - | 120 | 5 | 60 | 1 | CSA | NEMA 12 | JBA-L86
Note on B4: ASSET HIERARCHY LEVEL: Indicate whether parent asset, child asset, or component.
Note on C4: RELATIONSHIP: If child asset or component, indicate of which parent asset using the tag ID of the parent asset.
Note on D4: ASSET_NO: Synergen Asset ID given at time of hierarchy structure if migrated. Synergen generated if Asset data entered manually.
Note on E4: TAGGED: Use Validation drop down list to select appropriate value. Does the Asset have a Tag ID lamacoid?
Note on F4: ATTRIBUTE1: Smart numbered Tag_ID using City of Winnipeg standard format.
Note on G4: ASSET_RECORD_TYPE: Use Validation drop down list to select appropriate Asset Type. E = Equipment B = Building A = Virtual (used in Asset Hierarchy Structure)
Note on H4: ASSET_DESC: Asset Description Format: -Wastewater Process Area or Water Pumping or Collection Station -Type (HVAC, electrical, sump, clarifier, RAS etc.) -Tag_ID - Common Name (This is what everyone calls it) - Maximum data length = 2000 characters
Note on I4: ASSET_STATUS: Use Validation drop down list to select appropriate Asset Status. Format: Assets in service = ACTIVE
Note on J4: DEPARTMENT: Use Validation drop down list to select appropriate Department. (WWD)
Note on K4: AREA: Use Validation drop down list to select appropriate Area. (Water or Waste)
Note on L4: CRITICALITY: Use Validation drop down. Default the value = 6.
Note on M4: BUILDING: Use Validation drop down list to select appropriate Building. If no appropriate Building is listed provide proposed new Building to City of Winnipeg for consideration.
Note on N4: ROOM: Chlorine, Pump, Control, Motor etc. Name of room where the Asset is located. Maximum data length = 20 characters

## Electrical Equipment
Asset Type: | Electrical Equipment
Asset Type Code: | WW- ELEC EQPT
Asset Data Record | [12 empty] | Specification Data
ASSET HIERARCHY LEVEL | RELATIONSHIP | ASSET_NO - Asset Number | TAGGED - Asset Tag/Name Plate | TAG ID - Tag ID | ASSET_RECORD_TYPE - Asset Record Type | ASSET_DESC - Asset Description | ASSET_STATUS - Asset Status | DEPARTMENT - Administrative Department | AREA - Administrative Area | CRITICALITY - Asset Criticality Rating | BUILDING - Building Number | ROOM - Room (location) | MANUFACTURER - Manufacturer | MAKE - Make | MODEL_NO - Model | CAT_NO - Catalog/spec/type number | SERIAL_NO - Serial Number | DATEMFR - Date of Manufacture (DD/MM/YYYY) | POWER - Rated Power (kVA) | VOLT_PRIM - Primary Voltage (V) | VOLT_SEC - Secondary Voltage (V) | VOLT - Rated Voltage (V) | VOLT_CTRL - Control Voltage (V) | AMP - Rated Current (A) | AMP_SCCR - Rated Short Circuit Current (A) | FREQ - Frequency (Hz) | PHASE - Number of Phases | CONN_WIRE - Wiring Configuration (# of wires in connection) | REV - R.P.M. | EFF - Efficiency (%) | POWER_FACTR - Power Factor | INSUL_RATG - Insulation Temperature Rating (⁰C) | TEMP_RISE - Rated Temperature Rise (⁰C) | IMPED_PERC - Percentage Impedance (%) | CERTIF - Certification (CSA, UL, FM, Class, Div, Grp, Haz/Non-Haz) | ENCL_PROT - Enclosure Protection Code (NEMA/IP rating) | Attachment File Name to be Added to Asset
Parent | - |  | Yes | ATS-L72 | E | Automatic Transfer Switch ATS-L72 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Generac | Transfer System Data | GTS060N-3L2LDNBY | - | 3002553784 | 43115 | - | - | - | 600 | - | 800 | - | 60 | 3 | 4 | - | - | - | - | - | - | CSA | NEMA 1 | ATS-L72
Parent | - |  | No | CSTE-L70 | E | Customer Service Term End CSTE-L70 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Outside | Strong Electric | - | CSTE 4636 | CSTE 4636-8-3-34-M-P | S1414614 A | 20/11/2017 | - | - | - | 347/600 | - | 800 | 50000 | 60 | 3 | 4 | - | - | - | - | - | - | cETL | NEMA 3R | CSTE-L70
Parent | - |  | No | ELB-L74 | E | Emergency Lighting ELB-L74 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | Ready-Lite | MR16 LED | - | NMM2-L07 | - | - | - | - | - | 12 | - | - | - | - | - | - | - | - | - | - | - | - | CSA | - | ELB-L74
Parent | - |  | Yes | GEN-L72 | E | Standby Generator GEN-L72 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Generac | SG200 | SG0200LG20142S18HPNLE | - | 3002549048 | 43111 | 250 | - | - | 346/600 | - | 240 | - | 60 | 3 | 4 | 1800 | 91.0 | 0.8 | - | 130 | - | cETL | - | GEN-L72
Parent | - |  | Yes | MCC-L72E | E | Emergency Motor Control Center MCC-L72E | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | Square D | - | Model 6 | - | 40258921-001 | - | - | - | - | 600 | 120 | 600 | 25000 | 60 | 3 | 4 | - | - | - | - | - | - | CSA | NEMA 1 | MCC-L72E
Parent | - |  | Yes | PNL-L73E | E | Distribution Panelboard PNL-L73E | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Square D | NQ | - | 12402589210100001 | - | - | - | - | - | 120/208 | - | 100 | 10000 | 60 | 3 | 4 | - | - | - | - | - | - | CSA | NEMA 1 | PNL-L73E
Parent | - |  | Yes | SGR-L71 | E | Main Switchgear SGR-L71 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | Square D | Switchgear Unit | QED | - | 40258921-004 | 2/2018 | - | - | - | 600 | - | 600 | 25000 | 60 | 3 | 4 | - | - | - | - | - | - | CSA | NEMA 1 | SGR-L71
Parent | - |  | Yes | TVSS-L71 | E | Surge Suppressor TVSS-L71 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | Square D | QED Switchboard | - | TVS8IMA32 | - | - | - | - | - | 347/600 | - | 240,000 | - | - | 3 | - | - | - | - | - | - | - | - | NEMA 1 | TVSS-L71
Parent | - |  | Yes | VFD-L01 | E | Variable Frequency Drive VFD-L01 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | Schneider Electric | Altivar Process | ATV61HC11Y | 40258921-014 | 2F1803000068 | - | - | - | - | 575 | - | 125 | - | 60 | 3 | 3 | - | - | - | - | - | - | cUL | NEMA 1 | VFD-L01
Parent | - |  | Yes | VFD-L02 | E | Variable Frequency Drive VFD-L02 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | Schneider Electric | Altivar Process | ATV61HC11Y | 40258921-014 | 2F1803000070 | - | - | - | - | 575 | - | 125 | - | 60 | 3 | 3 | - | - | - | - | - | - | cUL | NEMA 1 | VFD-L02
Parent | - |  | Yes | VFD-L03 | E | Variable Frequency Drive VFD-L03 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | Schneider Electric | Altivar Process | ATV61HC11Y | 40258921-014 | 2F1803000071 | - | - | - | - | 575 | - | 125 | - | 60 | 3 | 3 | - | - | - | - | - | - | cUL | NEMA 1 | VFD-L03
Parent | - |  | Yes | XFMR-L73E | E | Transformer XFMR-L73E | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Square D | Sorgel Three Phase General Purpose Transformer | 33760-17212-010 | EE30T65HFCU | 006500199935 | - | 30 | 600 | 120/208 | - | - | 28.9 | - | 60 | 3 | 4 | - | 97.5 | - | 220 | 115 | 3.1 | cUL | NEMA 3R | XFMR-L73E
Note on B4: ASSET HIERARCHY LEVEL: Indicate whether parent asset, child asset, or component.
Note on C4: RELATIONSHIP: If child asset or component, indicate of which parent asset using the tag ID of the parent asset.
Note on D4: ASSET_NO: Synergen Asset ID given at time of hierarchy structure if migrated. Synergen generated if Asset data entered manually.
Note on E4: TAGGED: Use Validation drop down list to select appropriate value. Does the Asset have a Tag ID lamacoid?
Note on F4: ATTRIBUTE1: Smart numbered Tag_ID using City of Winnipeg standard format.
Note on G4: ASSET_RECORD_TYPE: Use Validation drop down list to select appropriate Asset Type. E = Equipment B = Building A = Virtual (used in Asset Hierarchy Structure)
Note on H4: ASSET_DESC: Asset Description Format: -Wastewater Process Area or Water Pumping or Collection Station -Type (HVAC, electrical, sump, clarifier, RAS etc.) -Tag_ID - Common Name (This is what everyone calls it) - Maximum data length = 2000 characters
Note on I4: ASSET_STATUS: Use Validation drop down list to select appropriate Asset Status. Format: Assets in service = ACTIVE
Note on J4: DEPARTMENT: Use Validation drop down list to select appropriate Department. (WWD)
Note on K4: AREA: Use Validation drop down list to select appropriate Area. (Water or Waste)
Note on L4: CRITICALITY: Use Validation drop down. Default the value = 6.
Note on M4: BUILDING: Use Validation drop down list to select appropriate Building. If no appropriate Building is listed provide proposed new Building to City of Winnipeg for consideration.
Note on N4: ROOM: Chlorine, Pump, Control, Motor etc. Name of room where the Asset is located. Maximum data length = 20 characters

## HVAC
Asset Type: | HVAC
Asset Type Code: | WW-HVAC
Asset Data Record | [12 empty] | Specification Data
ASSET HIERARCHY LEVEL | RELATIONSHIP | ASSET_NO - Asset Number | TAGGED - Asset Tag/Name Plate | TAG ID - Tag ID | ASSET_RECORD_TYPE - Asset Record Type | ASSET_DESC - Asset Description | ASSET_STATUS - Asset Status | DEPARTMENT - Administrative Department | AREA - Administrative Area | CRITICALITY - Asset Criticality Rating | BUILDING - Building Number | ROOM - Room (location) | MANUFACTURER - Manufacturer | MAKE - Make | MODEL_NO - Model | CAT_NO - Catalog/spec/type number | SERIAL_NO - Serial Number | DATEMFR - Date of Manufacture (DD/MM/YYYY) | POWER - Rated Power (kW, kVA, HP) | VOLT - Rated Voltage (V) | AMP - Rated Current (A) | FREQ - Frequency (Hz) | PHASE - Number of Phases | TYPE_CTRL - Control Type (on/off, modulating) | SIGNL_CTRL - Control Signal (mA, V, process, network, local) | POSN_FAIL - Fail Position (open, close, last) | TORQUE_MAX - Maximum Output Torque (Nm) | FLOW_GAS - Gas Flow Rate (m3/hr, cfm) | CERTIF - Certification (CSA, UL, FM, Class, Div, Grp, Haz/Non-Haz) | Attachment File Name to be Added to Asset
Parent | - |  | No | AHU-L65 | E | Outdoor Air Conditioner AHU-L65 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Outside | Bard Manufacturing Co, Inc. | - | W36LA-B09ZPXXXJ | EHW3TA-B09L | 310M173492481-02 | - | 9 kW | 208 | 21.7 | 60 | 3 | - | - | - | - | 1100 | cETL | AHU-L65
Parent | - |  | No | FV-L621 | E | Vent. Supply Damper Actuator FV-L621 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Belimo | FSAFB24-SR-S | 4011 | - | - | 27/2/2017 | - | 24 | - | 60 | - | Modulating | 0 - 10 V | Closed | 20 | - | cUL | FV-L621
Parent | - |  | No | FV-L622 | E | Vent. Return Damper Actuator FV-L622 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Belimo | LF24-SR-S | - | - | - | 20/3/2018 | - | 24 | - | 60 | - | Modulating | 0 - 10 V | Open | 4 | - | cUL | FV-L622
Parent | - |  | No | FV-L623 | E | Vent. Exhaust Damper Actuator FV-L623 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Belimo | LF24-SR-S | - | - | - | - | - | 24 | - | 60 | - | Modulating | 0 - 10 V | Closed | 4 | - | cUL | FV-L623
Parent | - |  | Yes | HCE-L63 | E | Ventilation Duct Heater HCE-L63 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Thermolec | - | FC-CTPBX | - | 371536-001 | - | 40 kW | 575 | 40 | 60 | 3 | - | - | - | - | 1800 | CSA | HCE-L63
Parent | - |  | No | SF-L62 | E | Ventilation Supply Fan SF-L62 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | - | - | - | - | - | - | 0.75 kW | 120 | - | 60 | 1 | - | - | - | - | 1800 | - | -
Parent | - |  | No | TV-L662-A | E | Gen. Supply Damper Actuator TV-L662-A | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Belimo | NFB24-MFT-S | 4011 | - | - | 2018-05-03 | - | 24 | - | 60 | - | Modulating | 0 - 10 V | Closed | 10 | - | cUL | TV-L662-A
Parent | - |  | No | TV-L662-B | E | Gen. Supply Damper Actuator TV-L662-B | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Belimo | FSAFB24-SR-S | 4011 | - | - | 27/2/2017 | - | 24 | - | 60 | - | Modulating | 0 - 10 V | Closed | 10 | - | cUL | TV-L662-B
Parent | - |  | No | TV-L663 | E | Gen. Return Damper Actuator TV-L663 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Belimo | NFB24-MFT-S | 4011 | - | 01809-40049-155-179 | 17/04/2018 | - | 24 | - | 60 | - | Modulating | 0 - 10 V | Closed | 10 | - | cUL | TV-L663
Parent | - |  | No | TV-L664 | E | Gen. Exhaust Damper Actuator TV-L664 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Belimo | AFB24-MFT-S | 4011 | - | 01806-40031-155-178 | 2018-06-04 | - | 24 | - | 60 | - | Modulating | 0 - 10 V | Open | 20 | - | cUL | TV-L664
Parent | - |  | No | UH-L64 | E | Main Floor Unit Heater UH-L64 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Ouellet | - | OAS10036AM-RT | - | 155221 | 2021-03-22 | 10 kW | 600 | 9.63 | 60 | 3 | - | - | - | - | 1800 | CSA | UH-L64
Parent | - |  | No | XV-L661 | E | Gen. Combustion Damper Actuator XV-L661 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Belimo | FSTF24-S US | - | - | - | 2017-04-02 | - | 24 | - | 60 | - | On/Off | 24 V | Open | 1 | - | cUL | XV-L661
Parent | - |  | No | - | E | Miscellaneous Duct Work | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Note on B4: ASSET HIERARCHY LEVEL: Indicate whether parent asset, child asset, or component.
Note on C4: RELATIONSHIP: If child asset or component, indicate of which parent asset using the tag ID of the parent asset.
Note on D4: ASSET_NO: Synergen Asset ID given at time of hierarchy structure if migrated. Synergen generated if Asset data entered manually.
Note on E4: TAGGED: Use Validation drop down list to select appropriate value. Does the Asset have a Tag ID lamacoid?
Note on F4: ATTRIBUTE1: Smart numbered Tag_ID using City of Winnipeg standard format.
Note on G4: ASSET_RECORD_TYPE: Use Validation drop down list to select appropriate Asset Type. E = Equipment B = Building A = Virtual (used in Asset Hierarchy Structure)
Note on H4: ASSET_DESC: Asset Description Format: -Wastewater Process Area or Water Pumping or Collection Station -Type (HVAC, electrical, sump, clarifier, RAS etc.) -Tag_ID - Common Name (This is what everyone calls it) - Maximum data length = 2000 characters
Note on I4: ASSET_STATUS: Use Validation drop down list to select appropriate Asset Status. Format: Assets in service = ACTIVE
Note on J4: DEPARTMENT: Use Validation drop down list to select appropriate Department. (WWD)
Note on K4: AREA: Use Validation drop down list to select appropriate Area. (Water or Waste)
Note on L4: CRITICALITY: Use Validation drop down. Default the value = 6.
Note on M4: BUILDING: Use Validation drop down list to select appropriate Building. If no appropriate Building is listed provide proposed new Building to City of Winnipeg for consideration.
Note on N4: ROOM: Chlorine, Pump, Control, Motor etc. Name of room where the Asset is located. Maximum data length = 20 characters

## Instruments
Asset Type: | Instruments
Asset Type Code: | WW-INSTR
Asset Data Record | [12 empty] | Specification Data
ASSET HIERARCHY LEVEL | RELATIONSHIP | ASSET_NO - Asset Number | TAGGED - Asset Tag/Name Plate | TAG ID - Tag ID | ASSET_RECORD_TYPE - Asset Record Type | ASSET_DESC - Asset Description | ASSET_STATUS - Asset Status | DEPARTMENT - Administrative Department | AREA - Administrative Area | CRITICALITY - Asset Criticality Rating | BUILDING - Building Number | ROOM - Room (location) | MANUFACTURER - Manufacturer | MAKE - Make | MODEL_NO - Model | CAT_NO - Catalog/spec/type number | SERIAL_NO - Serial Number | DATEMFR - Date of Manufacture (DD/MM/YYYY) | VOLT - Rated Voltage (V) | AMP - Rated Current (A) | FREQ - Frequency (Hz) | FLOW - Rated Flow (L/S) | SIGNAL_OUT - Output Signal Range (min - max mA/V) | TYPE_GAS - Gas Type for Analysis (ambient air, combustible, CO2, CO, H2S, flue gas) | PRESS_MAX - Rated Maximum Pressure (kPa, psi, bar) | CERTIF - Certification (CSA, UL, FM, Class, Div, Grp, Haz/Non-Haz) | ENCL_PROT - Enclosure Protection Code (NEMA/IP rating) | Attachment File Name to be Added to Asset
Parent | - |  | Yes | AIT-L550 | E | Generator Gas Detector AIT-L550 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | MSA | TRIGARD Gas Monitor | - | A-TRIGARD-A-M-0-0-38-5-00-0-00-0-1-2-0 | A-18-401078552-010-001 | - | - | - | - | - | 4 - 20mA HART | Methane (CH4) | - | - | NEMA 1 | AIT-L550
Parent | - |  | Yes | FIT-L011 | E | Pump P-L01 Flow Transmitter FIT-L011 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | Siemens | Sitrans F M MAG 6000 | 7ME6920-1AA30-1AA0 | - | N1K1095203 | 01/2018 | 24 | - | 50/60 | 405 | 4 - 20mA HART | - | - | CSA | NEMA 6 | FIT-L011
Parent | - |  | Yes | FIT-L021 | E | Pump P-L02 Flow Transmitter FIT-L021 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | Siemens | Sitrans F M MAG 6000 | 7ME6920-1AA30-1AA0 | - | N1K1095172 | 01/2018 | 24 | - | 50/60 | 405 | 4 - 20mA HART | - | - | CSA | NEMA 6 | FIT-L021
Parent | - |  | Yes | FIT-L031 | E | Pump P-L03 Flow Transmitter FIT-L031 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | Siemens | Sitrans F M MAG 6000 | 7ME6920-1AA30-1AA0 | - | N1K1095189 | 01/2018 | 24 | - | 50/60 | 405 | 4 - 20mA HART | - | - | CSA | NEMA 6 | FIT-L031
Parent | - |  | Yes | FSL-L012 | E | Pump P-L01 Seal Water Flow FSL-L012 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | John Crane | - | SFD Model | 20000581 | - | - | - | - | - | - | Off/On | - | - | - | NEMA 1 | FSL-L012
Parent | - |  | Yes | FSL-L022 | E | Pump P-L02 Seal Water Flow FSL-L022 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | John Crane | - | SFD Model | 20000581 | 4617 | - | - | - | - | - | Off/On | - | - | - | NEMA 1 | FSL-L022
Parent | - |  | Yes | FSL-L032 | E | Pump P-L03 Seal Water Flow FSL-L032 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | John Crane | - | SFD Model | 20000581 | 0618 | - | - | - | - | - | Off/On | - | - | - | NEMA 1 | FSL-L032
Parent | - |  | Yes | LIC-L500 | E | Wet Well Level Controller LIC-L500 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | Precision Digital | 1/8 DIN Process Digital Panel Meter | PD6000-7H7 | - | 1709-0243314 | - | 24 | - | - | - | 4 - 20mA | - | - | cUL | NEMA 1 | LIC-L500
Parent | - |  | Yes | LIT-L500-A | E | Wet Well Level Transmitter LIT-L500-A | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | Siemens | Sitrans P | PTB01ATEX2055 | - | - | - | - | - | - | - | 4 - 20mA HART | - | - | CSA | NEMA 4X | LIT-L500-A
Parent | - |  | Yes | LIT-L500-B | E | Wet Well Level Transmitter LIT-L500-B | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | Siemens | Sitrans P | PTB01ATEX2055 | - | - | - | - | - | - | - | 4 - 20mA HART | - | - | CSA | NEMA 4X | LIT-L500-B
Parent | - |  | Yes | PDSH-L611 | E | Differential Pressure Switch PDSH-L61 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Ashcroft | - | DDSN42GSBA25L | - | NSR-1.5IWDNSR | 2018-02-08 | 125/250/480 | 15 | - | - | Off/On | - | 50 psi | UL | NEMA 4 | PDSH-L611
Parent | - |  | Yes | TIC-L660 | E | Generator Temp Controller TIC-L660 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Honeywell | - | T775U2006 | - | 17460747U2006 | - | 24 | - | - | - | 0 - 10V | - | - | - | NEMA 1 | TIC-L660
Parent | - |  | Yes | TT-L601 | E | Main Floor Temp Transmitter TT-L601 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Main Floor | Siemens | - | 7MC1027-1AA | - | 11077087-0010-001 | - | - | - | - | - | 4 - 20mA | - | - | - | NEMA 4 | TT-L601
Parent | - |  | Yes | UIC-L600 | E | HVAC Temp. Controller UIC-L600 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Generator Room | Honeywell | - | T775U2006 | - | 19070543H2006 | - | 24 | - | - | - | 0 - 10V | - | - | - | NEMA 1 | UIC-L600
Parent | - |  | No | YV-L012 | E | Pump P-L01 Seal Water Valve YV-L012 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | ASCO | Red-Hat | Shutoff Valve 104R | 8210G001 | T190589 | - | 120 | - | 50/60 | - | - | - | - | CSA | NEMA 4 | YV-L012
Parent | - |  | No | YV-L022 | E | Pump P-L02 Seal Water Valve YV-L022 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | ASCO | Red-Hat | Shutoff Valve 104R | 8210G001 | T33175505 | - | 120 | - | 50/60 | - | - | - | - | CSA | NEMA 4 | YV-L022
Parent | - |  | No | YV-L032 | E | Pump P-L03 Seal Water Valve YV-L032 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | ASCO | Red-Hat | Shutoff Valve 104R | 8210G001 | T196158 | - | 120 | - | 50/60 | - | - | - | - | CSA | NEMA 4 | YV-L032
Note on B4: ASSET HIERARCHY LEVEL: Indicate whether parent asset, child asset, or component.
Note on C4: RELATIONSHIP: If child asset or component, indicate of which parent asset using the tag ID of the parent asset.
Note on D4: ASSET_NO: Synergen Asset ID given at time of hierarchy structure if migrated. Synergen generated if Asset data entered manually.
Note on E4: TAGGED: Use Validation drop down list to select appropriate value. Does the Asset have a Tag ID lamacoid?
Note on F4: ATTRIBUTE1: Smart numbered Tag_ID using City of Winnipeg standard format.
Note on G4: ASSET_RECORD_TYPE: Use Validation drop down list to select appropriate Asset Type. E = Equipment B = Building A = Virtual (used in Asset Hierarchy Structure)
Note on H4: ASSET_DESC: Asset Description Format: -Wastewater Process Area or Water Pumping or Collection Station -Type (HVAC, electrical, sump, clarifier, RAS etc.) -Tag_ID - Common Name (This is what everyone calls it) - Maximum data length = 2000 characters
Note on I4: ASSET_STATUS: Use Validation drop down list to select appropriate Asset Status. Format: Assets in service = ACTIVE
Note on J4: DEPARTMENT: Use Validation drop down list to select appropriate Department. (WWD)
Note on K4: AREA: Use Validation drop down list to select appropriate Area. (Water or Waste)
Note on L4: CRITICALITY: Use Validation drop down. Default the value = 6.
Note on M4: BUILDING: Use Validation drop down list to select appropriate Building. If no appropriate Building is listed provide proposed new Building to City of Winnipeg for consideration.
Note on N4: ROOM: Chlorine, Pump, Control, Motor etc. Name of room where the Asset is located. Maximum data length = 20 characters

## Motors
Asset Type: | Motors
Asset Type Code: | WW-MOTORS
Asset Data Record | [12 empty] | Specification Data
ASSET HIERARCHY LEVEL | RELATIONSHIP | ASSET_NO - Asset Number | TAGGED - Asset Tag/Name Plate | TAG ID - Tag ID | ASSET_RECORD_TYPE - Asset Record Type | ASSET_DESC - Asset Description | ASSET_STATUS - Asset Status | DEPARTMENT - Administrative Department | AREA - Administrative Area | CRITICALITY - Asset Criticality Rating | BUILDING - Building Number | ROOM - Room (location) | MANUFACTURER - Manufacturer | MAKE - Make | SERIAL_NO - Serial Number | DATEMFR - Date of Manufacture | WEIGHT - Weight (kg, lb) | TYPE_COOL - Cooling Type (convection, fan cooled, liquid cooled) | VOLT - Rated Voltage (V) | AMP - Rated Current (A) | FREQ - Frequency (Hz) | PHASE - Number of Phases | HORSEPOWER - Rate Horsepower (HP) | REV - R.P.M. | EFF - Efficiency (%) | POWER_FACTR - Power Factor (%) | SERV_FACTR - Service Factor | INSUL_CLASS - Insulation Class (A/B/F/N/H) | VFD_RATED - Rated for VFD Applications (Y/N) | CERTIF - Certification (CSA, UL, FM, Class, Div, Grp, Haz/Non-Haz) | FRAME_MOTR - Electric Motor Frame Size (NEMA code) | DESIGN_NEMA - Motor NEMA Design Code (A,B,C,D) | TEMP_AMBMAX - Maximum Ambient Temperature (⁰C) | Attachment File Name to be Added to Asset
Parent | - |  | Yes | MTR-L01 | E | Lift Pump Motor MTR-L01 | Active | WWD | Waste | 6 | 5719 Roblin Blvd | Motor Room | NIDEC Motor Corporation | TVCI | Y 09 20170117-0001 R 0003 | 2017-05-06 | 2300 lbs | TEFC | 575 | 118 | 60 | 3 | 125 | 1185 | 95.4 | 83 | 1.15 | F | Y | CSA | G | B | 40 | MTR-L01
Parent | - |  | Yes | MTR-L02 | E | Lift Pump Motor MTR-L02 | Active | WWD | Waste | 6 | 5719 Roblin Blvd | Motor Room | NIDEC Motor Corporation | TVCI | Y 09 20170117-0001 R 0002 | 2017-05-06 | 2300 lbs | TEFC | 575 | 118 | 60 | 3 | 125 | 1185 | 95.4 | 83 | 1.15 | F | Y | CSA | G | B | 40 | MTR-L02
Parent | - |  | Yes | MTR-L03 | E | Lift Pump Motor MTR-L03 | Active | WWD | Waste | 6 | 5719 Roblin Blvd | Motor Room | NIDEC Motor Corporation | TVCI | Y 09 20170117-0001 R 0001 | 2017-05-06 | 2300 lbs | TEFC | 575 | 118 | 60 | 3 | 125 | 1185 | 95.4 | 83 | 1.15 | F | Y | CSA | G | B | 40 | MTR-L03
Note on B4: ASSET HIERARCHY LEVEL: Indicate whether parent asset, child asset, or component.
Note on C4: RELATIONSHIP: If child asset or component, indicate of which parent asset using the tag ID of the parent asset.
Note on D4: ASSET_NO: Synergen Asset ID given at time of hierarchy structure if migrated. Synergen generated if Asset data entered manually.
Note on E4: TAGGED: Use Validation drop down list to select appropriate value. Does the Asset have a Tag ID lamacoid?
Note on F4: ATTRIBUTE1: Smart numbered Tag_ID using City of Winnipeg standard format.
Note on G4: ASSET_RECORD_TYPE: Use Validation drop down list to select appropriate Asset Type. E = Equipment B = Building A = Virtual (used in Asset Hierarchy Structure)
Note on H4: ASSET_DESC: Asset Description Format: -Wastewater Process Area or Water Pumping or Collection Station -Type (HVAC, electrical, sump, clarifier, RAS etc.) -Tag_ID - Common Name (This is what everyone calls it) - Maximum data length = 2000 characters
Note on I4: ASSET_STATUS: Use Validation drop down list to select appropriate Asset Status. Format: Assets in service = ACTIVE
Note on J4: DEPARTMENT: Use Validation drop down list to select appropriate Department. (WWD)
Note on K4: AREA: Use Validation drop down list to select appropriate Area. (Water or Waste)
Note on L4: CRITICALITY: Use Validation drop down. Default the value = 6.
Note on M4: BUILDING: Use Validation drop down list to select appropriate Building. If no appropriate Building is listed provide proposed new Building to City of Winnipeg for consideration.
Note on N4: ROOM: Chlorine, Pump, Control, Motor etc. Name of room where the Asset is located. Maximum data length = 20 characters

## Process Piping & Valves
Asset Type: | Process Piping & Valves
Asset Type Code: | WW-PROC PIPE & VALVE
Asset Data Record | [12 empty] | Specification Data
ASSET HIERARCHY LEVEL | RELATIONSHIP | ASSET_NO - Asset Number | TAGGED - Asset Tag/Name Plate | TAG ID - Tag ID | ASSET_RECORD_TYPE - Asset Record Type | ASSET_DESC - Asset Description | ASSET_STATUS - Asset Status | DEPARTMENT - Administrative Department | AREA - Administrative Area | CRITICALITY - Asset Criticality Rating | BUILDING - Building Number | ROOM - Room (location) | MANUFACTURER - Manufacturer | MAKE - Make | MODEL_NO - Model | CAT_NO - Catalog/spec/type number | SERIAL_NO - Serial Number | STYLE_STEM - Stem Style (rising, non-rising) | MATL_BODY - Body Construction Material (steel, stainless steel, copper, brass, cast iron) | MATL_DISKVALV - Valve Disk Material (316 stainless steel, carbon steel) | MATL_STEM - Stem Material (stainless steel, carbon steel) | WEIGHT - Weight (kg, lb) | SIZE_VALV - Valve Size (mm, in, manufacturer code) | TYPE_CHKVALV - Check Valve Type (swing, wafer, ball, center guided globe) | PRESS_MAX - Rated Maximum Pressure (kPa, psi, bar) | CERTIF - Certification (CSA, UL, FM, Class, Div, Grp, Haz/Non-Haz) | Attachment File Name to be Added to Asset
Parent | - |  | No | CV-L01 | E | P-L01 Check Valve CV-L01 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | DeZurik | CRF Rubber Flapper Swing Check Valves | 170853 | - | - | - | Ducticle Iron | - | - | 950 lbs | 400 mm | Swing | - | - | CV-L01
Parent | - |  | No | CV-L02 | E | P-L02 Check Valve CV-L02 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | DeZurik | CRF Rubber Flapper Swing Check Valves | 170853 | - | - | - | - | - | - | - | - | - | - | - | CV-L02
Parent | - |  | No | CV-L03 | E | P-L03 Check Valve CV-L03 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | DeZurik | CRF Rubber Flapper Swing Check Valves | 170853 | - | - | - | - | - | - | - | - | - | - | - | CV-L03
Parent | - |  | No | DV-P-L01 | E | P-L01 Discharge Valve DV-P-L01 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Motor Room | SCI | Metal Seat Solid Wedge Valve | N0001 | - | 170930 | Non-Rising | Ducticle Iron | Ducticle Iron | Stainless Steel 316 | - | 400 mm | - | 250 psi | - | DV-P-L01
Parent | - |  | No | DV-P-L02 | E | P-L02 Discharge Valve DV-P-L02 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Motor Room | Henry Pratt Company | Metal Seat Solid Wedge Valve | AWWAC500 | PLGDCL125 | 170920 | - | - | - | - | - | - | - | - | - | DV-P-L02
Parent | - |  | No | DV-P-L03 | E | P-L03 Discharge Valve DV-P-L03 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Motor Room | Henry Pratt Company | Metal Seat Solid Wedge Valve | AWWAC500 | PLGDCL125 | 171018 | - | - | - | - | - | - | - | - | - | DV-P-L03
Parent | - |  | No | UIV-P-L01 | E | P-L01 Upstream Iso Valve UIV-P-L01 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | Henry Pratt Company | Rising Stem Gate Valve | 400C-170960 | - | 400-171016-H | Rising | Ducticle Iron | Ducticle Iron | Stainless Steel 316 | - | - | - | - | - | UIV-P-L01
Parent | - |  | No | UIV-P-L02 | E | P-L02 Upstream Iso Valve UIV-P-L02 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | Henry Pratt Company | Rising Stem Gate Valve | 400C-170960 | - | 400-171016-H | - | - | - | - | - | - | - | - | - | UIV-P-L02
Parent | - |  | No | UIV-P-L03 | E | P-L03 Upstream Iso Valve UIV-P-L03 | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | Henry Pratt Company | Rising Stem Gate Valve | 400C-170960 | - | 400-DI140401-PT | - | - | - | - | - | - | - | - | - | UIV-P-L03
Parent | - |  | No | - | E | Lift Pump P-L01 Sanitary Piping | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | - | - | - | - | - | - | Ducticle Iron | - | - | - | - | - | - | - | -
Parent | - |  | No | - | E | Lift Pump P-L02 Sanitary Piping | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Parent | - |  | No | - | E | Lift Pump P-L03 Sanitary Piping | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Parent | - |  | No | - | E | Potable Water Piping | Active | WWD | Waste | 6 | 5719 Roblin Boulevard | Pump Room | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Note on B4: ASSET HIERARCHY LEVEL: Indicate whether parent asset, child asset, or component.
Note on C4: RELATIONSHIP: If child asset or component, indicate of which parent asset using the tag ID of the parent asset.
Note on D4: ASSET_NO: Synergen Asset ID given at time of hierarchy structure if migrated. Synergen generated if Asset data entered manually.
Note on E4: TAGGED: Use Validation drop down list to select appropriate value. Does the Asset have a Tag ID lamacoid?
Note on F4: ATTRIBUTE1: Smart numbered Tag_ID using City of Winnipeg standard format.
Note on G4: ASSET_RECORD_TYPE: Use Validation drop down list to select appropriate Asset Type. E = Equipment B = Building A = Virtual (used in Asset Hierarchy Structure)
Note on H4: ASSET_DESC: Asset Description Format: -Wastewater Process Area or Water Pumping or Collection Station -Type (HVAC, electrical, sump, clarifier, RAS etc.) -Tag_ID - Common Name (This is what everyone calls it) - Maximum data length = 2000 characters
Note on I4: ASSET_STATUS: Use Validation drop down list to select appropriate Asset Status. Format: Assets in service = ACTIVE
Note on J4: DEPARTMENT: Use Validation drop down list to select appropriate Department. (WWD)
Note on K4: AREA: Use Validation drop down list to select appropriate Area. (Water or Waste)
Note on L4: CRITICALITY: Use Validation drop down. Default the value = 6.
Note on M4: BUILDING: Use Validation drop down list to select appropriate Building. If no appropriate Building is listed provide proposed new Building to City of Winnipeg for consideration.
Note on N4: ROOM: Chlorine, Pump, Control, Motor etc. Name of room where the Asset is located. Maximum data length = 20 characters

## Pumps
Asset Type: | Pumps
Asset Type Code: | WW-PUMPS
Asset Data Record | [12 empty] | Specification Data
ASSET HIERARCHY LEVEL | RELATIONSHIP | ASSET_NO - Asset Number | TAGGED - Asset Tag/Name Plate | TAG ID - Tag ID | ASSET_RECORD_TYPE - Asset Record Type | ASSET_DESC - Asset Description | ASSET_STATUS - Asset Status | DEPARTMENT - Administrative Department | AREA - Administrative Area | CRITICALITY - Asset Criticality Rating | BUILDING - Building Number | ROOM - Room (location) | MANUFACTURER - Manufacturer | MAKE - Make | MODEL_NO - Model | SERIAL_NO - Serial Number | DATEMFR - Date of Manufacture | WEIGHT - Weight (kg, lb) | DIAM_IMPELR - Impeller Diameter (mm, in) | DIAM_SHFT - Shaft Diameter (mm, in) | MATL_CASE - Case Material (steel, stainless steel, cast iron, aluminum) | MATL_IMPELR - Impeller Material (steel, stainless steel, aluminum) | SIZE_FLNGSUCT - Suction Flange Size (mm, in, manufacturer code) | SIZE_FLNGDISCH - Discharge Flange Size (mm, in, manufacturer code) | SEAL_PUMP - Pump Seal Type (mechanical, gland) | VOLT - Rated Voltage (V) | AMP - Rated Current (A) | FREQ - Frequency (Hz) | POWER - Rated Power (kW, kVA, HP) | FLOW_FLUID - Fluid Flow Rate (l/min, m3/hr, USGPM) | REV - R.P.M. | HEAD_PUMP - Pump Head (m, ft) | EFF - Efficiency (%) | CERTIF - Certification (CSA, UL, FM, Class, Div, Grp, Haz/Non-Haz) | Attachment File Name to be Added to Asset
Parent | - |  | Yes | P-L01 | E | Lift Pump P-L01 | Active | WWD | Waste | 6 | 5719 Roblin Blvd | Pump Room | Flowserve | Solids Handling Pumps | 14MNV16A-FR7L | 1711MS006693-2 | - | 3000 lbs | 361 mm | 152.3 mm | Cast Iron A278 | Cast Iron A278 | 406.4 mm | 355.6 mm | Mechanical Cartridge Dual | - | - | - | 93.25 kW | 1620 m3/hr | 1190 | 13 m | 80 | - | P-L01
Parent | - |  | Yes | P-L02 | E | Lift Pump P-L02 | Active | WWD | Waste | 6 | 5719 Roblin Blvd | Pump Room | Flowserve | Solids Handling Pumps | 14MNV16A-FR7L | 1711MS006693-1 | - | 3000 lbs | 361 mm | 152.3 mm | Cast Iron A278 | Cast Iron A278 | 406.4 mm | 355.6 mm | Mechanical Cartridge Dual | - | - | - | 93.25 kW | 1620 m3/hr | 1190 | 13 m | 80 | - | P-L02
Parent | - |  | Yes | P-L03 | E | Lift Pump P-L03 | Active | WWD | Waste | 6 | 5719 Roblin Blvd | Pump Room | Flowserve | Solids Handling Pumps | 14MNV16A-FR7L | 1711MS006693-3 | - | 3000 lbs | 361 mm | 152.3 mm | Cast Iron A278 | Cast Iron A278 | 406.4 mm | 355.6 mm | Mechanical Cartridge Dual | - | - | - | 93.25 kW | 1620 m3/hr | 1190 | 13 m | 80 | - | P-L03
Parent | - |  | No | P-L12 | E | Pump Room Sump Pump P-L12 | Active | WWD | Waste | 6 | 5719 Roblin Blvd | Pump Room | Liberty Pumps | Vertical Magnetic Float Switch | 257 | 1483LF | 2021-09-07 | - | - | - | - | - | - | - | - | 115 | 5.2 | 60 | 1/3 HP | - | - | - | - | CSA | P-L12
Note on B4: ASSET HIERARCHY LEVEL: Indicate whether parent asset, child asset, or component.
Note on C4: RELATIONSHIP: If child asset or component, indicate of which parent asset using the tag ID of the parent asset.
Note on D4: ASSET_NO: Synergen Asset ID given at time of hierarchy structure if migrated. Synergen generated if Asset data entered manually.
Note on E4: TAGGED: Use Validation drop down list to select appropriate value. Does the Asset have a Tag ID lamacoid?
Note on F4: ATTRIBUTE1: Smart numbered Tag_ID using City of Winnipeg standard format.
Note on G4: ASSET_RECORD_TYPE: Use Validation drop down list to select appropriate Asset Type. E = Equipment B = Building A = Virtual (used in Asset Hierarchy Structure)
Note on H4: ASSET_DESC: Asset Description Format: -Wastewater Process Area or Water Pumping or Collection Station -Type (HVAC, electrical, sump, clarifier, RAS etc.) -Tag_ID - Common Name (This is what everyone calls it) - Maximum data length = 2000 characters
Note on I4: ASSET_STATUS: Use Validation drop down list to select appropriate Asset Status. Format: Assets in service = ACTIVE
Note on J4: DEPARTMENT: Use Validation drop down list to select appropriate Department. (WWD)
Note on K4: AREA: Use Validation drop down list to select appropriate Area. (Water or Waste)
Note on L4: CRITICALITY: Use Validation drop down. Default the value = 6.
Note on M4: BUILDING: Use Validation drop down list to select appropriate Building. If no appropriate Building is listed provide proposed new Building to City of Winnipeg for consideration.
Note on N4: ROOM: Chlorine, Pump, Control, Motor etc. Name of room where the Asset is located. Maximum data length = 20 characters